## 119_161
S&C Power Fuses - Type SMD 1-A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD 1-A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD 1-A (69 kV)
Slow Speed (TCC 119-1-6-1) | [9 empty] | Slow Speed (TCC 119-1-6-1) | [9 empty] | Slow Speed (TCC 119-1-6-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
12001.9 | 0.015792 | 12001.9 | 0.015792 | 12001.9 | 0.015903 | 12001.9 | 0.015998 | 12001.9 | 0.016302 | 12001.9 | 0.016597 | 12001.9 | 0.016997 | 12001.9 | 0.018005 | 12001.9 | 0.019494 | 11730.4 | 0.022629 | 11730.4 | 0.026429 | 11730.4 | 0.028293 | 11723.7 | 0.032294
11034.8 | 0.016597 | 11302.9 | 0.0164 | 11508.2 | 0.016302 | 11965.9 | 0.015998 | 11439.3 | 0.016796 | 10762.4 | 0.017898 | 11485.2 | 0.017598 | 11450.8 | 0.018698 | 11670.5 | 0.020004 | 10509.9 | 0.02558 | 10655.2 | 0.029416 | 10802.6 | 0.031275 | 10534 | 0.03701
9602.8 | 0.018005 | 9875.49 | 0.017703 | 10075 | 0.017598 | 10538.7 | 0.017304 | 10004.7 | 0.018293 | 9328.3 | 0.019591 | 10054.8 | 0.019301 | 10024.7 | 0.020691 | 10247.7 | 0.022403 | 8887.63 | 0.03076 | 9224.43 | 0.03483 | 9303.94 | 0.037609 | 8964.24 | 0.046432
8174.72 | 0.019708 | 8449 | 0.019398 | 8645.59 | 0.019206 | 9107.08 | 0.018791 | 8576.7 | 0.020104 | 7901.44 | 0.022006 | 8628.31 | 0.021509 | 8593.87 | 0.023404 | 8811.43 | 0.025694 | 7425.96 | 0.037587 | 7876.79 | 0.042366 | 7990.29 | 0.046273 | 7554.54 | 0.059636
6739.84 | 0.02181 | 7014.92 | 0.021509 | 7214.12 | 0.021296 | 7683.25 | 0.020794 | 7142.33 | 0.022492 | 6469.08 | 0.025189 | 7199.7 | 0.024498 | 7163.79 | 0.027299 | 7381.97 | 0.030603 | 6064.27 | 0.047808 | 6768.51 | 0.051918 | 6760.77 | 0.058419 | 6461.95 | 0.07529
5312.3 | 0.024693 | 5584.68 | 0.024304 | 5783.62 | 0.023992 | 6252.82 | 0.023404 | 5714.62 | 0.026002 | 5043.11 | 0.030091 | 5766.29 | 0.029005 | 5731.79 | 0.033498 | 7264.8 | 0.031186 | 5072.73 | 0.059397 | 5756.57 | 0.065246 | 5866.31 | 0.072414 | 5455.11 | 0.098207
3884.56 | 0.029005 | 4153.75 | 0.028406 | 4353.65 | 0.028014 | 4821.19 | 0.027191 | 4284.54 | 0.031497 | 3611.07 | 0.039308 | 4336.27 | 0.036887 | 5523.58 | 0.034614 | 6979.93 | 0.032386 | 4228.78 | 0.075983 | 4966.46 | 0.081388 | 4926.83 | 0.094889 | 4776.92 | 0.12229
2452.2 | 0.036413 | 2726.42 | 0.035414 | 2924.12 | 0.034787 | 3390.58 | 0.033498 | 2854.78 | 0.042517 | 3532.49 | 0.040017 | 4263.17 | 0.037515 | 5285.8 | 0.036197 | 6639.5 | 0.034204 | 3692.47 | 0.093113 | 4163.94 | 0.1072 | 4272.56 | 0.11973 | 4041.87 | 0.16303
1023.2 | 0.058195 | 1295.57 | 0.054394 | 1494.75 | 0.052119 | 1960.06 | 0.047899 | 2778.72 | 0.043499 | 3421.24 | 0.041105 | 4112.42 | 0.038803 | 5038.07 | 0.037889 | 6334.64 | 0.03591 | 3154.83 | 0.11939 | 3553.58 | 0.13824 | 3686.14 | 0.15413 | 3503.11 | 0.21059
969.419 | 0.060074 | 1233.62 | 0.056095 | 1456.39 | 0.053112 | 1921.24 | 0.048618 | 2653.79 | 0.044993 | 3260.89 | 0.042813 | 3955.12 | 0.040216 | 4787.55 | 0.039898 | 5847.59 | 0.039191 | 2720.26 | 0.15281 | 2950.52 | 0.19083 | 3196.62 | 0.19762 | 3011.94 | 0.27579
885.978 | 0.063827 | 1144.47 | 0.059127 | 1374.32 | 0.05521 | 1844.06 | 0.050188 | 2514.28 | 0.047097 | 3074.05 | 0.045083 | 3739.71 | 0.042306 | 4499.73 | 0.042601 | 5496.03 | 0.04218 | 2380.71 | 0.19226 | 2433.04 | 0.26724 | 2788.02 | 0.2515 | 2626.94 | 0.35422
820.315 | 0.067277 | 1060.71 | 0.062509 | 1294.28 | 0.057791 | 1762.91 | 0.052016 | 2377.34 | 0.049397 | 2912.45 | 0.04752 | 3543.11 | 0.044504 | 4241.91 | 0.045488 | 5170.78 | 0.045217 | 2070.47 | 0.24792 | 2099.1 | 0.34958 | 2473.76 | 0.31408 | 2247.02 | 0.47819
765.619 | 0.070703 | 975.253 | 0.066612 | 1191.18 | 0.061524 | 1668.57 | 0.054286 | 2225.5 | 0.052483 | 2737.35 | 0.050388 | 3360.2 | 0.04691 | 3982.9 | 0.048715 | 4830.84 | 0.049006 | 1819.3 | 0.3148 | 1858.23 | 0.43832 | 2172.42 | 0.40017 | 1916.55 | 0.65336
701.121 | 0.075569 | 886.865 | 0.071907 | 1100.7 | 0.065497 | 1560.43 | 0.05722 | 2070.89 | 0.055983 | 2567.64 | 0.053696 | 3174.02 | 0.049692 | 3709.91 | 0.052797 | 4554.05 | 0.052692 | 1558.85 | 0.42207 | 1616.08 | 0.57371 | 1975.56 | 0.47682 | 1625.35 | 0.90713
634.397 | 0.081901 | 807.294 | 0.077778 | 974.278 | 0.072625 | 1453.48 | 0.060795 | 1944.44 | 0.059599 | 2403.64 | 0.057391 | 3010.17 | 0.052587 | 3469.47 | 0.057107 | 4149.6 | 0.059303 | 1349.52 | 0.56136 | 1382.35 | 0.79018 | 1775.08 | 0.58399 | 1395.06 | 1.2515
572.877 | 0.089471 | 744.478 | 0.08371 | 853.794 | 0.081738 | 1349.8 | 0.064978 | 1814.79 | 0.063827 | 2241.13 | 0.061891 | 2806.65 | 0.056598 | 3234.91 | 0.0622 | 3830.55 | 0.065888 | 1164.96 | 0.75264 | 1181.07 | 1.0772 | 1591.3 | 0.72805 | 1343.36 | 1.3591
509.62 | 0.099603 | 685.864 | 0.090544 | 761.8 | 0.091721 | 1267.38 | 0.068901 | 1688.71 | 0.068627 | 2100.08 | 0.066414 | 2637.92 | 0.060674 | 2971.29 | 0.069106 | 3582.3 | 0.072194 | 1025.4 | 0.975 | 998.193 | 1.5276 | 1429.81 | 0.90609 | 1172.99 | 1.8369
456.989 | 0.11121 | 637.577 | 0.09716 | 692.757 | 0.1013 | 1169.93 | 0.074377 | 1557.31 | 0.074896 | 1936.68 | 0.07277 | 2410.86 | 0.067277 | 2742.83 | 0.07678 | 3313.49 | 0.080369 | 880.623 | 1.3299 | 850.901 | 2.19 | 1292.83 | 1.1161 | 1023.05 | 2.5242
412.26 | 0.12418 | 586.206 | 0.10625 | 624.952 | 0.11367 | 1085.39 | 0.08013 | 1433.27 | 0.081982 | 1785.98 | 0.08021 | 2218.83 | 0.074377 | 2547.18 | 0.084714 | 3098.75 | 0.088675 | 771.142 | 1.7718 | 747.678 | 2.9633 | 1167.63 | 1.3906 | 914.517 | 3.3267
362.001 | 0.14413 | 535.75 | 0.11746 | 560.971 | 0.12934 | 983.087 | 0.088939 | 1316.47 | 0.090634 | 1661.91 | 0.087798 | 2075.03 | 0.081011 | 2325.61 | 0.096105 | 2877.71 | 0.098815 | 671.804 | 2.4488 | 671.804 | 3.9098 | 1050.34 | 1.7678 | 814.223 | 4.5531
330.182 | 0.16173 | 496.54 | 0.12832 | 507.585 | 0.14673 | 892.202 | 0.099307 | 1209.19 | 0.1005 | 1558.87 | 0.09506 | 1898.33 | 0.090724 | 2121.19 | 0.10946 | 2565.08 | 0.11758 | 585.598 | 3.4469 | 615.841 | 4.9332 | 949.716 | 2.2433 | 742.137 | 5.9731
293.136 | 0.18922 | 456.532 | 0.14186 | 474.215 | 0.16061 | 793.685 | 0.11378 | 1129.69 | 0.10946 | 1456.39 | 0.10395 | 1734.93 | 0.10251 | 1942.5 | 0.12517 | 2363.12 | 0.13365 | 522.571 | 4.6693 | 557.477 | 6.6369 | 853.339 | 2.9061 | 681.094 | 8.1007
253.821 | 0.23103 | 416.82 | 0.15982 | 440.829 | 0.17756 | 731.197 | 0.12642 | 1038.67 | 0.12246 | 1359.28 | 0.1139 | 1598.34 | 0.11481 | 1773.52 | 0.14385 | 2161.88 | 0.15405 | 463.666 | 6.7057 | 508.122 | 9.2306 | 739.17 | 4.3071 | 643.951 | 10.2681
221.544 | 0.28349 | 379.802 | 0.18149 | 400.075 | 0.20345 | 673.628 | 0.14116 | 967.482 | 0.13485 | 1256.02 | 0.1268 | 1466.62 | 0.12985 | 1627.37 | 0.16384 | 1987.69 | 0.17668 | 420.927 | 9.1569 | 466.327 | 13.0752 | 662.641 | 5.9424 | 606.746 | 13.9095
199.86 | 0.33266 | 345.035 | 0.20671 | 363.816 | 0.23404 | 615.647 | 0.15918 | 901.169 | 0.14893 | 1161.77 | 0.14242 | 1383.97 | 0.14186 | 1503.75 | 0.18605 | 1825.71 | 0.20325 | 384.32 | 12.8231 | 438.13 | 17.5104 | 601.217 | 8.2175 | 581.258 | 17.8342
178.504 | 0.40097 | 315.968 | 0.23544 | 334.168 | 0.26683 | 554.834 | 0.18458 | 838.563 | 0.16531 | 1079.98 | 0.15824 | 1296.87 | 0.15636 | 1390.91 | 0.21065 | 1715.95 | 0.22604 | 362.53 | 17.1236 | 411.166 | 25.3059 | 545.174 | 11.808 | 557.796 | 24.2559
162.977 | 0.46632 | 290.8 | 0.26683 | 305.405 | 0.30725 | 506.571 | 0.21127 | 772.541 | 0.18642 | 1007.97 | 0.17633 | 1218.9 | 0.17235 | 1278.84 | 0.2428 | 1568.25 | 0.26366 | 341.194 | 25.3785 | 396.608 | 34.576 | 507.831 | 16.6402 | 538.97 | 32.2058
150.145 | 0.53696 | 266.302 | 0.30694 | 280.798 | 0.35344 | 450.185 | 0.25289 | 721.752 | 0.20753 | 926.76 | 0.20064 | 1144.47 | 0.19035 | 1179.33 | 0.2782 | 1478.4 | 0.29236 | 327.61 | 36.614 | 383.88 | 49.7691 | 477.397 | 24.2976 | 518.698 | 46.9183
139.714 | 0.61097 | 247.306 | 0.34546 | 258.431 | 0.40457 | 406.122 | 0.29852 | 668.261 | 0.23473 | 817.04 | 0.24547 | 1068.16 | 0.21254 | 1094.11 | 0.31623 | 1402.08 | 0.32225 | 318.917 | 50.3137 | 375.623 | 73.8461 | 459.441 | 35.3367 | 506.38 | 65.666
121.218 | 0.7871 | 226.926 | 0.3974 | 238.8 | 0.46308 | 379.422 | 0.33465 | 623.08 | 0.26236 | 734.862 | 0.29323 | 984.07 | 0.24352 | 1021.16 | 0.35626 | 1303.37 | 0.36777 | 311.343 | 71.3926 | 368.386 | 117.702 | 446.482 | 50.835 | 496.908 | 98.2178
107.833 | 0.97838 | 207.601 | 0.46125 | 224.219 | 0.51758 | 340.238 | 0.40136 | 575.748 | 0.29823 | 668.261 | 0.34375 | 923.984 | 0.27083 | 952.125 | 0.40336 | 1217.68 | 0.41846 | 306.395 | 102.469 | 366.284 | 179.1 | 435.63 | 76.603 | 490.972 | 140.246
97.4738 | 1.1828 | 189.164 | 0.54017 | 210.528 | 0.5762 | 309.092 | 0.47473 | 541.134 | 0.33134 | 605.269 | 0.40779 | 860.652 | 0.30573 | 888.64 | 0.45624 | 1129.69 | 0.48233 | 303.95 | 141.214 | 365.028 | 267.73 | 429.196 | 115.036 | 487.055 | 225.983
89.2623 | 1.4116 | 165.771 | 0.69038 | 196.884 | 0.64657 | 288.195 | 0.53749 | 502.534 | 0.37552 | 549.313 | 0.4857 | 803.267 | 0.34443 | 824.427 | 0.52016 | 1054.37 | 0.54991 | 302.216 | 196.287 | 364.82 | 370.018 | 426.259 | 177.67 | 485.385 | 332.059
81.3349 | 1.6963 | 148.354 | 0.84294 | 178.861 | 0.77009 | 270.327 | 0.60015 | 465.755 | 0.42856 | 500.528 | 0.57448 | 749.708 | 0.38997 | 765.619 | 0.59836 | 969.419 | 0.64721 | 301.87 | 262.417 | 364.402 | 497.806 | 426.259 | 264.832 | 484.83 | 467.681
75.1564 | 2.0004 | 134.639 | 1.012 | 166.435 | 0.8806 | 254.838 | 0.66348 | 429.944 | 0.49397 | 460.199 | 0.6648 | 702.525 | 0.43759 | 723.197 | 0.66282 | 915.705 | 0.72842 | 301.352 | 361.845 | 365.237 | 595.196 | 425.772 | 382.734 | 485.385 | 557.259
70.2154 | 2.3195 | 122.192 | 1.2234 | 155.805 | 1.002 | 236.424 | 0.7587 | 398.08 | 0.56542 | 420.589 | 0.78087 | 640.133 | 0.51912 | 675.652 | 0.75045 | 854.649 | 0.83877 | 300.663 | 470.097 |  |  | 425.042 | 514.324 | 484.83 | 597.245
66.2585 | 2.6577 | 110.784 | 1.4968 | 145.416 | 1.1492 | 222.21 | 0.8539 | 368.208 | 0.6485 | 387.475 | 0.90904 | 582.117 | 0.622 | 622.457 | 0.87798 | 803.267 | 0.95533 | 300.835 | 571.807 |  |  | 424.555 | 595.537
62.3998 | 3.0572 | 99.9415 | 1.8642 | 134.101 | 1.3566 | 206.153 | 0.98325 | 325.591 | 0.81495 | 362.001 | 1.0333 | 532.012 | 0.74082 | 583.282 | 0.99012 | 743.734 | 1.1255 | 300.491 | 597.929
59.1194 | 3.4891 | 93.4645 | 2.153 | 124.785 | 1.573 | 194.341 | 1.1022 | 297.566 | 0.96391 | 337.864 | 1.1828 | 497.534 | 0.84546 | 550.963 | 1.1088 | 698.322 | 1.2819
55.6764 | 4.0376 | 87.3199 | 2.5139 | 114.731 | 1.8922 | 183.023 | 1.2406 | 272.226 | 1.1469 | 314.392 | 1.3647 | 468.09 | 0.95533 | 516.288 | 1.2567 | 649.808 | 1.4893
52.1202 | 4.8185 | 82.1523 | 2.8947 | 108.482 | 2.1381 | 173.749 | 1.381 | 252.303 | 1.3312 | 292.843 | 1.5777 | 437.754 | 1.1 | 491.107 | 1.3879 | 610.131 | 1.7014
49.1339 | 5.705 | 77.2133 | 3.3598 | 103.088 | 2.3779 | 164.121 | 1.5512 | 235.244 | 1.5359 | 276.064 | 1.7845 | 414.741 | 1.232 | 468.558 | 1.5313 | 577.478 | 1.9187
46.3651 | 6.6944 | 73.7418 | 3.7852 | 98.3551 | 2.6262 | 155.493 | 1.7407 | 222.655 | 1.7269 | 257.657 | 2.0691 | 394.908 | 1.3647 | 444.37 | 1.7184 | 551.515 | 2.1381
44.1478 | 7.7855 | 69.6559 | 4.4108 | 93.2777 | 2.9764 | 147.91 | 1.9359 | 209.269 | 1.9728 | 242.894 | 2.3708 | 372.653 | 1.5512 | 420.168 | 1.9513 | 527.246 | 2.359
42.2051 | 8.8939 | 66.0601 | 5.0942 | 89.2623 | 3.3332 | 139.714 | 2.2006 | 196.687 | 2.2492 | 229.666 | 2.6976 | 355.188 | 1.7269 | 399.276 | 2.2006 | 498.032 | 2.7003
40.6313 | 10.2311 | 62.5247 | 5.9717 | 85.0787 | 3.7739 | 132.369 | 2.4989 | 183.023 | 2.6603 | 219.559 | 3.018 | 335.172 | 1.9708 | 381.706 | 2.4522 | 470.907 | 3.0786
39.3123 | 11.7927 | 59.5347 | 7.0074 | 81.8244 | 4.2013 | 126.671 | 2.7792 | 174.271 | 2.9793 | 207.601 | 3.4821 | 322.351 | 2.1573 | 362.726 | 2.7737 | 446.151 | 3.4925
37.8086 | 14.3987 | 56.9149 | 8.2145 | 78.3803 | 4.7238 | 120.372 | 3.156 | 164.286 | 3.4306 | 197.871 | 3.9308 | 310.021 | 2.3661 | 344.001 | 3.1875 | 425.666 | 3.9503
36.6544 | 17.6683 | 54.5738 | 9.62 | 75.5331 | 5.3112 | 114.731 | 3.5697 | 155.028 | 3.9819 | 189.732 | 4.424 | 300.257 | 2.572 | 328.535 | 3.6053 | 408.975 | 4.389
35.6423 | 21.8315 | 52.5914 | 11.2771 | 73.3006 | 5.9245 | 110.012 | 3.9898 | 148.949 | 4.4549 | 183.206 | 4.9055 | 287.331 | 2.8519 | 313.137 | 4.1186 | 393.331 | 4.9055
35.0064 | 26.0023 | 50.8841 | 13.3385 | 70.5673 | 6.8832 | 105.171 | 4.5352 | 144.113 | 4.8763 | 178.147 | 5.3483 | 278.56 | 3.097 | 299.058 | 4.7473 | 377.908 | 5.4991
34.3132 | 32.6441 | 49.6277 | 15.5433 | 68.1401 | 7.9496 | 101.148 | 5.0841 | 138.601 | 5.407 | 171.504 | 6.0074 | 268.173 | 3.4238 | 287.906 | 5.3112 | 363.816 | 6.1219
33.8024 | 39.3467 | 48.354 | 18.6234 | 65.6649 | 9.3468 | 97.3764 | 5.6993 | 133.433 | 5.9955 | 165.937 | 6.7077 | 258.173 | 3.8002 | 278.282 | 5.9658 | 351.653 | 6.7747
33.4325 | 48.4735 | 47.5389 | 21.6803 | 63.5332 | 10.9351 | 94.027 | 6.4208 | 128.2 | 6.8084 | 161.678 | 7.423 | 249.792 | 4.1722 | 267.637 | 6.8017 | 337.864 | 7.6475
33.1993 | 60.1339 | 46.9718 | 25.3142 | 62.0265 | 12.4796 | 90.9746 | 7.1979 | 123.543 | 7.7546 | 156.899 | 8.371 | 240.718 | 4.6724 | 259.467 | 7.7085 | 328.535 | 8.4967
33.0668 | 79.0235 | 46.3187 | 29.7339 | 60.5555 | 14.4848 | 88.2857 | 8.093 | 119.772 | 8.7277 | 151.806 | 9.4777 | 233.137 | 5.1553 | 251.295 | 8.9382 | 319.782 | 9.4683
33.0007 | 108.271 | 45.812 | 34.7523 | 59.4157 | 16.8289 | 85.8479 | 9.1812 | 115.768 | 10.2209 | 147.762 | 10.8486 | 226.246 | 5.6824 | 244.112 | 10.2006 | 313.45 | 10.3435
33.0007 | 153.286 | 45.3108 | 40.9416 | 58.5311 | 19.4168 | 83.8959 | 10.395 | 112.234 | 11.8632 | 143.825 | 12.4425 | 219.779 | 6.2509 | 239.278 | 11.4692 | 304.795 | 11.8161
33.0007 | 221.153 | 44.9048 | 48.5699 | 57.6596 | 23.2877 | 81.5792 | 12.1012 | 109.135 | 13.6875 | 140.555 | 14.2423 | 212.219 | 7.1197 | 233.603 | 12.9726 | 298.759 | 13.1673
33.0007 | 317.486 | 44.547 | 58.7173 | 56.9149 | 27.6541 | 79.6445 | 14.0316 | 106.44 | 16.0294 | 136.947 | 16.7622 | 204.715 | 8.1091 | 229.666 | 14.5136 | 291.966 | 14.8049
32.9677 | 467.707 | 44.3691 | 72.553 | 56.2922 | 33.3985 | 77.9114 | 16.0613 | 104.541 | 18.3298 | 133.967 | 19.4361 | 198.466 | 9.2361 | 225.568 | 16.2216 | 285.327 | 16.8791
32.9348 | 545.559 | 44.1478 | 91.6296 | 55.7321 | 40.1363 | 76.8282 | 18.1306 | 102.471 | 21.4234 | 130.268 | 23.5435 | 192.215 | 10.6352 | 221.766 | 18.1847 | 279.677 | 19.0727
32.9019 | 600.146 | 44.1478 | 121.614 | 55.3433 | 49.3971 | 75.3822 | 21.3384 | 100.442 | 25.1388 | 127.944 | 27.8747 | 187.094 | 12.1373 | 216.507 | 21.3596 | 273.317 | 22.0495
|  | 44.1478 | 157.141 | 55.1775 | 62.5093 | 74.1114 | 24.8409 | 98.552 | 29.178 | 125.536 | 33.0355 | 182.11 | 14.3702 | 213.07 | 24.7916 | 266.569 | 26.0799
|  | 44.1478 | 198.261 | 55.1775 | 81.9006 | 73.1542 | 29.0623 | 97.3764 | 33.6315 | 123.667 | 38.7648 | 178.326 | 16.6295 | 209.269 | 29.4986 | 262.075 | 29.7339
|  | 44.1478 | 274.08 | 55.1775 | 111.103 | 72.065 | 34.4088 | 95.8307 | 39.9374 | 122.07 | 45.6688 | 174.445 | 19.3014 | 204.92 | 36.1968 | 257.657 | 34.7523
|  | 44.1478 | 356.969 | 55.1775 | 143.987 | 71.1342 | 41.3914 | 94.5929 | 46.8172 | 120.372 | 55.5401 | 170.138 | 23.2877 | 201.063 | 44.0645 | 253.567 | 39.3077
|  | 44.0596 | 437.592 | 55.1775 | 187.907 | 70.356 | 50.3382 | 93.3711 | 56.0946 | 119.056 | 65.7576 | 167.437 | 27.7366 | 197.673 | 54.0703 | 249.792 | 45.3974
|  | 44.0156 | 541.779 | 55.1775 | 253.645 | 69.5167 | 61.3406 | 92.627 | 65.9539 | 117.518 | 81.8193 | 164.615 | 33.266 | 195.12 | 63.5107 | 246.073 | 54.5017
|  | 43.9716 | 600.146 | 55.1775 | 345.457 | 68.9627 | 73.9354 | 91.7971 | 77.3153 | 116.116 | 103.229 | 162.326 | 40.0168 | 192.793 | 74.3035 | 242.894 | 63.637
|  |  |  | 55.1775 | 466.778 | 68.2765 | 90.9044 | 91.0656 | 91.9945 | 115.075 | 126.796 | 160.39 | 47.097 | 190.683 | 87.1898 | 239.517 | 76.3992
|  |  |  | 55.1775 | 566.546 | 67.8002 | 113.671 | 90.5208 | 108.702 | 113.476 | 168.122 | 158.476 | 56.3739 | 188.22 | 102.616 | 236.187 | 91.6296
|  |  |  | 55.1223 | 600.146 | 67.3946 | 140.735 | 90.0693 | 131.543 | 112.684 | 205.072 | 156.429 | 67.7467 | 186.721 | 118.044 | 232.671 | 113.784
[6 empty] | 66.9914 | 180.228 | 89.7098 | 152.982 | 112.122 | 254.908 | 154.718 | 80.3693 | 185.048 | 137.011 | 229.666 | 135.926
[6 empty] | 66.724 | 228.523 | 88.8171 | 188.093 | 111.563 | 314.348 | 152.262 | 103.024 | 183.573 | 161.252 | 227.153 | 161.733
[6 empty] | 66.4576 | 295.279 | 88.551 | 239.207 | 111.117 | 384.962 | 150.295 | 130.631 | 181.746 | 191.677 | 224.443 | 196.692
[6 empty] | 66.2585 | 365.582 | 88.1093 | 310.007 | 110.453 | 487.148 | 148.206 | 168.959 | 180.298 | 226.939 | 222.21 | 237.314
[6 empty] | 66.1923 | 452.174 | 88.0213 | 415.975 | 110.232 | 569.933 | 146.731 | 205.684 | 178.861 | 269.223 | 220.439 | 280.971
[6 empty] | 66.0601 | 540.166 | 88.0213 | 527.965 | 110.012 | 600.146 | 145.416 | 269.223 | 177.969 | 311.55 | 218.683 | 330.684
[6 empty] | 66.0601 | 600.146 | 88.0213 | 573.91 |  |  | 144.402 | 324.501 | 176.905 | 372.177 | 216.94 | 414.326
[8 empty] | 88.0213 | 600.146 |  |  | 143.538 | 405.772 | 175.846 | 451.725 | 215.858 | 496.923
[12 empty] | 142.965 | 501.884 | 175.144 | 532.178 | 215.642 | 566.546
[12 empty] | 142.537 | 572.77 | 174.445 | 573.91 | 215.211 | 600.146
[12 empty] | 142.537 | 600.146 | 173.922 | 600.146