## 153_44S4
S&C Power Fuses - Type SM-4 (3E thru 200E) and Type SM-5 (3E thru 300E) (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SM-4 (3E thru 200E) and Type SM-5 (3E thru 300E) (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SM-4 (3E thru 200E) and Type SM-5 (3E thru 300E) (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SM-4 (3E thru 200E) and Type SM-5 (3E thru 300E) (25 and 34.5 kV)
Standard Speed (TCC 153-4-4) | [9 empty] | Standard Speed (TCC 153-4-4) | [9 empty] | Standard Speed (TCC 153-4-4) | [9 empty] | Standard Speed (TCC 153-4-4)
Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
| 3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25346.6 | 0.015602 | 25346.6 | 0.015635 | 25346.6 | 0.015651 | 25346.6 | 0.015667 | 25346.6 | 0.015799 | 25346.6 | 0.015832 | 25320.1 | 0.015898 | 25346.6 | 0.015915 | 25373.1 | 0.015981 | 25320.1 | 0.016048 | 25346.6 | 0.016132 | 25346.6 | 0.016183 | 25293.7 | 0.016233 | 25320.1 | 0.016301 | 25293.7 | 0.016541 | 25373.1 | 0.016576 | 25320.1 | 0.016645 | 25320.1 | 0.017666 | 25320.1 | 0.018477 | 25346.6 | 0.019652
10756.1 | 0.019346 | 17397.5 | 0.017265 | 15186.9 | 0.017908 | 16528.8 | 0.017501 | 18836 | 0.017032 | 18008.1 | 0.017265 | 17108.9 | 0.017464 | 18737.8 | 0.017265 | 17653.9 | 0.017428 | 17506.9 | 0.017611 | 20097.2 | 0.016979 | 17727.9 | 0.017593 | 18178.3 | 0.017428 | 20160.3 | 0.017301 | 22033.6 | 0.017446 | 21918.8 | 0.017648 | 21398.1 | 0.018058 | 18994.2 | 0.019879 | 20055.2 | 0.020662 | 21510.2 | 0.022113
4456.03 | 0.024039 | 6278.47 | 0.022228 | 6084.64 | 0.022438 | 10049.5 | 0.019796 | 10028.5 | 0.019879 | 10326.4 | 0.019796 | 8745.14 | 0.020683 | 12386.3 | 0.019085 | 7968.23 | 0.021364 | 11706.5 | 0.019508 | 12029 | 0.019266 | 11657.6 | 0.019611 | 13551.4 | 0.019125 | 16754.9 | 0.018458 | 18875.4 | 0.018381 | 18640.1 | 0.019125 | 17525.2 | 0.019983 | 13939.3 | 0.023493 | 15507.7 | 0.024368 | 16842.7 | 0.026769
1932.93 | 0.029622 | 3179.15 | 0.026188 | 2908.86 | 0.026937 | 6193.73 | 0.022368 | 5989.97 | 0.022603 | 5940.09 | 0.022769 | 4967.77 | 0.023914 | 7714.16 | 0.021543 | 5367.31 | 0.023789 | 8094.16 | 0.021475 | 8708.65 | 0.021386 | 8883.34 | 0.021746 | 10835.1 | 0.020791 | 13523.1 | 0.019879 | 14966.2 | 0.020171 | 15123.5 | 0.02112 | 14733.4 | 0.021952 | 9882.86 | 0.030152 | 11903.9 | 0.030596 | 13201.8 | 0.033506
1046.47 | 0.034392 | 1535.81 | 0.031275 | 2851.65 | 0.027134 | 3139.52 | 0.026353 | 3634.3 | 0.02546 | 3420.5 | 0.026188 | 3596.51 | 0.026243 | 4952.22 | 0.024317 | 3992.82 | 0.02627 | 6371.03 | 0.023104 | 6670.91 | 0.023371 | 7043.56 | 0.023864 | 8901.93 | 0.022603 | 9638 | 0.022984 | 11333.2 | 0.02296 | 12674.4 | 0.023128 | 12464.2 | 0.024266 | 7690.01 | 0.038417 | 9369.78 | 0.039024 | 10144.5 | 0.044978
752.876 | 0.037467 | 1264.44 | 0.03302 | 1828.75 | 0.030437 | 1902.85 | 0.030247 | 2365.01 | 0.028859 | 2430.17 | 0.029406 | 2905.82 | 0.028262 | 3757.93 | 0.02638 | 3277 | 0.028678 | 4885.38 | 0.025327 | 4880.27 | 0.026435 | 5190.74 | 0.027592 | 6818.97 | 0.025327 | 6963.03 | 0.02722 | 8119.58 | 0.028115 | 9872.53 | 0.027078 | 9965.85 | 0.028351 | 5667.14 | 0.054278 | 7252.77 | 0.052825 | 7610.04 | 0.066189
539.39 | 0.040731 | 978.754 | 0.035896 | 1244.77 | 0.033964 | 1351.92 | 0.033893 | 1900.87 | 0.031079 | 1838.33 | 0.032405 | 2292 | 0.030982 | 3036.24 | 0.028889 | 2760.73 | 0.030982 | 4102.83 | 0.027248 | 3445.62 | 0.031047 | 3897.96 | 0.032541 | 4531.18 | 0.032304 | 5278.29 | 0.032848 | 5964.98 | 0.036273 | 8230.68 | 0.031112 | 7976.57 | 0.034428 | 4368.4 | 0.07717 | 5971.22 | 0.068224 | 5805.04 | 0.10019
319.156 | 0.047389 | 704.156 | 0.040056 | 990.073 | 0.037 | 1050.85 | 0.037663 | 1502.47 | 0.033822 | 1384.82 | 0.036463 | 1608.1 | 0.035972 | 2205.04 | 0.03302 | 2214.28 | 0.034464 | 2905.82 | 0.031935 | 2642.14 | 0.036198 | 3026.73 | 0.03931 | 3195.81 | 0.042735 | 3757.93 | 0.044141 | 4550.17 | 0.047986 | 6458.2 | 0.039146 | 6271.91 | 0.043865 | 4055.92 | 0.086202 | 5067.43 | 0.087471 | 4535.92 | 0.15086
206.608 | 0.053939 | 477.794 | 0.046264 | 743.491 | 0.04103 | 754.452 | 0.043093 | 1036.67 | 0.039392 | 944.578 | 0.043546 | 1110.72 | 0.043183 | 1504.04 | 0.040392 | 1759.37 | 0.039516 | 2150.41 | 0.038058 | 1996.59 | 0.044557 | 2265.79 | 0.050929 | 2497.13 | 0.054905 | 2970.31 | 0.057307 | 3460.06 | 0.065913 | 5311.5 | 0.04849 | 4602.79 | 0.064821 | 3165.89 | 0.12593 | 4102.83 | 0.12141 | 3420.5 | 0.2467
147.404 | 0.060821 | 345.185 | 0.053101 | 505.013 | 0.048897 | 539.954 | 0.052004 | 735.76 | 0.046652 | 640.26 | 0.055482 | 807.496 | 0.053491 | 1035.59 | 0.052825 | 1335.07 | 0.048338 | 1593.04 | 0.047886 | 1532.61 | 0.057187 | 1609.78 | 0.075971 | 1777.85 | 0.084862 | 2287.21 | 0.08021 | 2642.14 | 0.094992 | 4120.02 | 0.066744 | 3522.1 | 0.094992 | 2481.52 | 0.18844 | 3093.91 | 0.19668 | 2714.94 | 0.38449
107.163 | 0.069157 | 238.669 | 0.064619 | 338.397 | 0.060758 | 401.68 | 0.064014 | 577.918 | 0.053827 | 437.629 | 0.07847 | 615.326 | 0.06794 | 705.63 | 0.076688 | 1055.26 | 0.059502 | 1107.24 | 0.06851 | 1242.17 | 0.072408 | 1216.47 | 0.11238 | 1350.51 | 0.12752 | 1748.37 | 0.11841 | 2079.67 | 0.13863 | 3318.37 | 0.09016 | 2783.91 | 0.13805 | 1947.12 | 0.29004 | 2337.98 | 0.33047 | 2079.67 | 0.6542
80.4739 | 0.079625 | 160.094 | 0.086292 | 234.711 | 0.080293 | 292.327 | 0.083195 | 439.004 | 0.066397 | 310.924 | 0.11754 | 482.815 | 0.088482 | 528.231 | 0.10995 | 811.728 | 0.079459 | 802.447 | 0.10209 | 951.515 | 0.10284 | 947.545 | 0.16555 | 1028.04 | 0.19854 | 1328.11 | 0.1857 | 2028.14 | 0.14424 | 2650.44 | 0.12859 | 2134.73 | 0.21404 | 1542.25 | 0.45063 | 1796.54 | 0.54722 | 1635.23 | 1.0855
60.3054 | 0.094597 | 113.268 | 0.12192 | 160.261 | 0.1223 | 216.559 | 0.11416 | 333.132 | 0.088574 | 241.177 | 0.16852 | 365.613 | 0.12765 | 428.127 | 0.14759 | 631.618 | 0.1096 | 606.386 | 0.15229 | 738.071 | 0.1507 | 734.991 | 0.25508 | 776.049 | 0.32602 | 1047.56 | 0.27934 | 1489.95 | 0.2421 | 2114.74 | 0.18609 | 1604.74 | 0.36039 | 1172.76 | 0.78372 | 1343.47 | 0.99334 | 1322.57 | 1.7863
44.9559 | 0.12002 | 85.5039 | 0.1737 | 116.998 | 0.18609 | 138.443 | 0.21027 | 254.65 | 0.12384 | 183.397 | 0.25803 | 283.006 | 0.18863 | 324.539 | 0.22907 | 525.477 | 0.14289 | 482.815 | 0.21947 | 563.599 | 0.23537 | 586.438 | 0.38329 | 604.487 | 0.52156 | 838.463 | 0.4215 | 1133 | 0.40173 | 1638.65 | 0.29095 | 1222.84 | 0.60555 | 934.756 | 1.3032 | 998.387 | 2.0718 | 1085.46 | 3.1524
34.6171 | 0.15845 | 63.3422 | 0.26679 | 90.186 | 0.27528 | 112.324 | 0.294 | 193.44 | 0.18493 | 135.437 | 0.43446 | 225.334 | 0.27328 | 252.002 | 0.35111 | 393.781 | 0.22247 | 378.445 | 0.33047 | 429.472 | 0.38289 | 439.004 | 0.66661 | 441.305 | 0.96472 | 673.909 | 0.64068 | 849.935 | 0.70234 | 1256.53 | 0.47876 | 961.514 | 0.9779 | 760.788 | 2.257 | 815.982 | 4.166 | 944.578 | 5.2692
25.833 | 0.22693 | 45.6664 | 0.45251 | 63.8741 | 0.48581 | 79.3048 | 0.5309 | 144.354 | 0.29585 | 104.946 | 0.6907 | 181.111 | 0.40299 | 195.677 | 0.55819 | 279.77 | 0.40215 | 299.128 | 0.51131 | 340.526 | 0.58872 | 337.338 | 1.1569 | 347.72 | 1.6312 | 538.827 | 1.0048 | 651.739 | 1.1912 | 888.082 | 0.94873 | 771.197 | 1.6058 | 633.602 | 4.4959 | 710.812 | 8.7161 | 854.389 | 8.5449
20.1011 | 0.32841 | 34.5087 | 0.73689 | 47.6661 | 0.81459 | 55.5253 | 1.0466 | 114.458 | 0.43673 | 79.8872 | 1.1618 | 142.257 | 0.63072 | 151.149 | 0.91756 | 193.238 | 0.79526 | 234.465 | 0.79859 | 264.692 | 0.97995 | 276.572 | 1.8164 | 276.861 | 3.052 | 413.178 | 1.8259 | 516.221 | 2.0226 | 694.652 | 1.5875 | 647.665 | 2.569 | 574.304 | 8.3858 | 666.205 | 15.723 | 799.935 | 13.9439
16.0551 | 0.48938 | 24.5945 | 1.4108 | 35.3485 | 1.4421 | 40.5361 | 2.0353 | 87.2191 | 0.71941 | 60.7483 | 2.0957 | 111.273 | 1.0175 | 119.971 | 1.474 | 139.168 | 1.553 | 180.355 | 1.3802 | 216.333 | 1.5498 | 223.458 | 3.3179 | 242.695 | 5.3636 | 348.448 | 2.8607 | 454.887 | 2.9149 | 549.636 | 3.0108 | 547.915 | 4.8979 | 541.084 | 14.0023 | 634.265 | 32.0482 | 767.177 | 21.8463
12.8369 | 0.7829 | 18.6827 | 2.5396 | 27.1907 | 2.5159 | 33.269 | 3.3773 | 66.6015 | 1.19 | 48.2678 | 3.8201 | 96.3253 | 1.3587 | 99.4978 | 2.2219 | 111.739 | 2.5878 | 143.902 | 2.3532 | 176.439 | 2.6702 | 190.033 | 5.8492 | 221.597 | 8.9935 | 304.491 | 4.5574 | 389.279 | 5.5458 | 464.498 | 5.7764 | 495.081 | 9.5649 | 515.682 | 24.3777 | 621.142 | 55.9121 | 742.714 | 39.3675
10.5026 | 1.2937 | 15.0791 | 4.5148 | 21.7859 | 4.4679 | 28.1451 | 6.2014 | 52.8633 | 1.8879 | 40.1986 | 8.0344 | 77.0172 | 2.1737 | 82.26 | 3.6182 | 92.4772 | 4.4585 | 120.473 | 3.9706 | 154.665 | 4.2229 | 166.755 | 11.5789 | 204.673 | 16.6003 | 279.478 | 6.8768 | 352.847 | 10.5955 | 433.985 | 9.6653 | 468.398 | 15.8714 | 502.905 | 40.3244 | 612.118 | 99.0853 | 730.396 | 79.4925
9.0728 | 2.2242 | 13.0262 | 7.8765 | 18.2771 | 8.3421 | 25.4046 | 11.0243 | 42.1788 | 3.2256 | 35.6826 | 20.4769 | 64.0747 | 3.4848 | 68.5081 | 7.2453 | 82.0025 | 7.4993 | 106.382 | 7.0439 | 138.878 | 6.8983 | 157.11 | 19.7214 | 195.677 | 27.3734 | 259.758 | 11.6882 | 333.132 | 20.5197 | 411.024 | 17.7105 | 452.516 | 25.1535 | 493.531 | 66.7723 | 606.386 | 174.863 | 731.924 | 152.667
8.0788 | 4.4261 | 11.7701 | 19.2937 | 16.2918 | 17.3989 | 23.4154 | 22.8257 | 36.4365 | 5.0274 | 33.6537 | 46.9651 | 54.3197 | 6.1691 | 60.9391 | 16.6697 | 75.9777 | 12.7597 | 96.83 | 13.9294 | 128.674 | 10.9326 | 150.361 | 34.0846 | 189.636 | 44.021 | 249.381 | 17.3083 | 318.823 | 43.6093 | 395.844 | 31.5172 | 439.923 | 47.7563 | 486.87 | 115.523 | 601.965 | 319.747 | 731.924 | 262.482
7.5481 | 8.6979 | 11.5145 | 43.3822 | 15.5594 | 37.1704 | 22.433 | 44.8562 | 32.6147 | 8.78 | 33.061 | 106.933 | 48.7241 | 11.7862 | 57.4141 | 32.7245 | 71.1353 | 24.2002 | 92.0914 | 26.336 | 121.867 | 17.0749 | 146.636 | 65.529 | 185.131 | 76.4002 | 239.669 | 27.7186 | 311.249 | 83.3168 | 385.633 | 52.0254 | 432.174 | 94.1432 | 484.838 | 183.85 | 601.336 | 495.753 | 731.16 | 415.555
7.2542 | 17.5082 | 11.5145 | 88.611 | 15.4945 | 81.5949 | 22.0379 | 81.6802 | 30.568 | 15.0955 | 33.061 | 241.447 | 45.571 | 25.9539 | 55.758 | 71.1636 | 68.0086 | 47.4581 | 89.2482 | 53.6249 | 116.51 | 27.7475 | 144.354 | 142.501 | 180.922 | 144.448 | 233.243 | 50.1061 | 307.369 | 137.387 | 378.841 | 84.8089 | 427.233 | 187.926 | 483.32 | 311.183 | 601.965 | 593.904 | 730.396 | 593.904
7.2164 | 35.8365 | 11.5266 | 169.47 | 15.5269 | 168.061 | 22.1534 | 173.408 | 29.4698 | 24.0993 | 33.1302 | 444.738 | 44.3491 | 53.513 | 55.2937 | 134.97 | 66.3236 | 88.3338 | 88.505 | 91.2399 | 113.149 | 47.0142 | 144.053 | 280.329 | 178.48 | 247.574 | 230.576 | 71.4615 | 304.173 | 263.581 | 373.728 | 128.64 | 425.45 | 353.829 | 484.332 | 459.849 | 601.965 | 593.904 | 730.396 | 593.904
7.2164 | 91.0496 | 11.5386 | 327.861 | 15.5432 | 321.085 | 22.1534 | 308.272 | 28.6497 | 41.1324 | 33.1648 | 599.512 | 44.0718 | 97.342 | 55.2937 | 273.106 | 66.3236 | 135.535 | 88.7829 | 175.962 | 111.04 | 80.3269 | 144.204 | 458.411 | 176.808 | 383.452 | 226.515 | 116.492 | 301.955 | 420.355 | 370.228 | 195.942 | 425.45 | 527.254 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904
7.2314 | 242.964 | 11.5386 | 524.509 | 15.5757 | 487.031 | 22.1997 | 525.057 | 28.56 | 80.4948 | 33.1648 | 599.512 | 44.0258 | 188.319 | 55.2359 | 493.171 | 66.4624 | 227.734 | 88.5975 | 307.951 | 110.231 | 144.147 | 144.354 | 594.525 | 174.97 | 552.62 | 222.991 | 187.143 | 300.695 | 590.195 | 365.613 | 318.747 | 426.787 | 597.013 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904
7.2466 | 594.525 | 11.5386 | 596.39 | 15.5757 | 595.146 | 22.223 | 598.886 | 28.5003 | 145.964 | 33.1648 | 599.512 | 44.1641 | 327.177 | 55.1782 | 600.765 | 66.4624 | 387.881 | 88.6902 | 533.345 | 110.231 | 255.452 | 144.354 | 594.525 | 174.97 | 599.512 | 221.365 | 328.546 | 300.695 | 590.195 | 364.087 | 470.044 | 426.787 | 597.013 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904
7.2466 | 594.525 | 11.5386 | 596.39 | 15.5757 | 595.146 | 22.223 | 598.886 | 28.5302 | 286.245 | 33.1648 | 599.512 | 44.2565 | 517.437 | 55.1782 | 600.765 | 66.6015 | 554.933 | 88.7829 | 598.261 | 110.346 | 450.345 | 144.354 | 594.525 | 174.97 | 599.512 | 220.442 | 529.461 | 300.695 | 590.195 | 363.327 | 594.525 | 426.787 | 597.013 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904
7.2466 | 594.525 | 11.5386 | 596.39 | 15.5757 | 595.146 | 22.223 | 598.886 | 28.5302 | 439.2 | 33.1648 | 599.512 | 44.3028 | 598.886 | 55.1782 | 600.765 | 66.6712 | 597.637 | 88.7829 | 598.261 | 110.346 | 598.261 | 144.354 | 594.525 | 174.97 | 599.512 | 219.751 | 599.512 | 300.695 | 590.195 | 363.327 | 594.525 | 426.787 | 597.013 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904
7.2466 | 594.525 | 11.5386 | 596.39 | 15.5757 | 595.146 | 22.223 | 598.886 | 28.5302 | 595.146 | 33.1648 | 599.512 | 44.3028 | 598.886 | 55.1782 | 600.765 | 66.6712 | 597.637 | 88.7829 | 598.261 | 110.346 | 598.261 | 144.354 | 594.525 | 174.97 | 599.512 | 219.751 | 599.512 | 300.695 | 590.195 | 363.327 | 594.525 | 426.787 | 597.013 | 485.853 | 593.904 | 601.965 | 593.904 | 730.396 | 593.904