## 167_62
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal Style | [9 empty] | Universal Style | [9 empty] | Universal Style | [9 empty] | Universal Style
"N" Speed (TCC 167-6-2) | [9 empty] | "N" Speed (TCC 167-6-2) | [9 empty] | "N" Speed (TCC 167-6-2) | [9 empty] | "N" Speed (TCC 167-6-2)
Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
5N |  | 8N |  | 10N |  | 15N |  | 20N |  | 25N |  | 30N |  | 40N |  | 45N |  | 50N |  | 65N |  | 75N |  | 85N |  | 95N |  | 100N |  | 125N |  | 150N |  | 200N
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013284 | 10000 | 0.013458 | 10000 | 0.013607 | 10000 | 0.013648 | 10000 | 0.013938 | 10000 | 0.014463 | 10000 | 0.015083 | 10000 | 0.015984 | 10000 | 0.018927 | 10000 | 0.022524 | 10000 | 0.038807
1352 | 0.013771 | 1350.65 | 0.013993 | 1350.65 | 0.014035 | 1661.27 | 0.01391 | 2393.09 | 0.013758 | 3678.79 | 0.013675 | 4244.33 | 0.01358 | 4308.48 | 0.013634 | 6363.54 | 0.013634 | 7512.62 | 0.013703 | 8684.89 | 0.013771 | 9030.29 | 0.014049 | 9084.64 | 0.014623 | 9333.26 | 0.015311 | 9296 | 0.016372 | 9314.61 | 0.019798 | 9398.82 | 0.023703 | 9398.82 | 0.041787
1167.17 | 0.013896 | 1168.34 | 0.014177 | 1199.11 | 0.014219 | 1488.22 | 0.014064 | 2103.46 | 0.013896 | 3153.73 | 0.013826 | 3678.79 | 0.013689 | 3855.83 | 0.013785 | 5649.6 | 0.013771 | 6784.12 | 0.013799 | 7819.22 | 0.013938 | 8179.12 | 0.014191 | 8211.9 | 0.014799 | 8641.57 | 0.015621 | 8693.58 | 0.016787 | 8719.7 | 0.020709 | 8745.9 | 0.02532 | 8860.34 | 0.044997
1012.66 | 0.014092 | 1050.83 | 0.014333 | 1091.53 | 0.014448 | 1308.11 | 0.014348 | 1918.58 | 0.014049 | 2760.98 | 0.013979 | 3163.2 | 0.013882 | 3509.89 | 0.013938 | 5030.83 | 0.013951 | 6163.13 | 0.013896 | 7110.59 | 0.01412 | 7512.62 | 0.014348 | 7542.73 | 0.015008 | 7921.53 | 0.016048 | 8057.35 | 0.017385 | 8081.56 | 0.021924 | 8162.78 | 0.027129 | 8428.21 | 0.048115
877.733 | 0.014333 | 944.205 | 0.01455 | 973.933 | 0.014814 | 1169.51 | 0.014637 | 1753.45 | 0.014233 | 2409.9 | 0.014162 | 2882.29 | 0.014078 | 3207.8 | 0.014106 | 4533.91 | 0.014177 | 5587.8 | 0.014092 | 6531.16 | 0.014319 | 6907.34 | 0.014506 | 6955.86 | 0.01525 | 7363.86 | 0.016504 | 7490.12 | 0.018004 | 7497.61 | 0.023373 | 7649.08 | 0.02895 | 7961.24 | 0.052122
815.942 | 0.014448 | 842.474 | 0.014799 | 889.218 | 0.015113 | 1059.27 | 0.014918 | 1610.56 | 0.014448 | 2090.88 | 0.014405 | 2589.81 | 0.014319 | 2961.17 | 0.01429 | 4081.99 | 0.014434 | 5066.17 | 0.014276 | 5992.96 | 0.014521 | 6300.22 | 0.014755 | 6524.63 | 0.015481 | 6750.29 | 0.017143 | 6893.54 | 0.018908 | 6928.09 | 0.025043 | 7110.59 | 0.031299 | 7475.15 | 0.057145
760.019 | 0.014623 | 759.259 | 0.015008 | 798.187 | 0.015496 | 958.474 | 0.015296 | 1461.68 | 0.014726 | 1790.66 | 0.014726 | 2265.02 | 0.014711 | 2703.6 | 0.014535 | 3689.85 | 0.014696 | 4648.69 | 0.014477 | 5559.93 | 0.01474 | 5757.97 | 0.014978 | 6053.19 | 0.015809 | 6231.3 | 0.017825 | 6466.18 | 0.019778 | 6446.81 | 0.026859 | 6649.79 | 0.033737 | 7082.2 | 0.062152
707.928 | 0.01477 | 698.086 | 0.01525 | 730.218 | 0.015841 | 859.493 | 0.015762 | 1331.87 | 0.015038 | 1634.9 | 0.014978 | 2008.89 | 0.015113 | 2409.9 | 0.014888 | 3256.28 | 0.015129 | 4240.09 | 0.01474 | 5030.83 | 0.015098 | 5278.2 | 0.015281 | 5660.91 | 0.016161 | 5717.8 | 0.01872 | 5975 | 0.020897 | 6016.98 | 0.028662 | 6175.47 | 0.03673 | 6696.5 | 0.067734
661.39 | 0.014933 | 646.351 | 0.015481 | 657.433 | 0.016372 | 753.209 | 0.016454 | 1208.75 | 0.015388 | 1485.25 | 0.015235 | 1758.72 | 0.015605 | 2174.03 | 0.015235 | 2928.78 | 0.015527 | 3844.27 | 0.015038 | 4579.48 | 0.015465 | 4814.27 | 0.015589 | 5309.96 | 0.01657 | 5320.59 | 0.01968 | 5548.82 | 0.022233 | 5627.05 | 0.030833 | 5729.25 | 0.04039 | 6401.84 | 0.072937
616.059 | 0.015129 | 598.45 | 0.015793 | 602.654 | 0.016837 | 664.705 | 0.017246 | 1082.84 | 0.015825 | 1362.86 | 0.015496 | 1570.8 | 0.016064 | 1978.99 | 0.015574 | 2700.9 | 0.015857 | 3481.92 | 0.015373 | 4077.91 | 0.015984 | 4470.88 | 0.01592 | 4955.93 | 0.01716 | 4980.77 | 0.020627 | 5096.66 | 0.023941 | 5194.42 | 0.033568 | 5390.21 | 0.043623 | 6053.19 | 0.080205
572.117 | 0.015357 | 555.764 | 0.016177 | 555.208 | 0.017385 | 593.682 | 0.018058 | 972.96 | 0.016372 | 1219.67 | 0.015952 | 1400.16 | 0.01672 | 1776.39 | 0.016016 | 2446.32 | 0.016389 | 3119.23 | 0.015857 | 3649.48 | 0.016553 | 4143.68 | 0.016356 | 4570.33 | 0.017914 | 4561.2 | 0.022144 | 4704.81 | 0.025883 | 4704.81 | 0.037697 | 5040.9 | 0.047923 | 5627.05 | 0.090431
531.84 | 0.015636 | 516.122 | 0.016686 | 514.576 | 0.017914 | 538.799 | 0.018833 | 875.104 | 0.017023 | 1114.7 | 0.016438 | 1301.59 | 0.017177 | 1569.23 | 0.01662 | 2220.17 | 0.017006 | 2865.05 | 0.016274 | 3368.9 | 0.017057 | 3875.15 | 0.016787 | 4214.73 | 0.018814 | 4257.09 | 0.023561 | 4351.78 | 0.027983 | 4395.52 | 0.041165 | 4648.69 | 0.053979 | 5288.77 | 0.10105
494.399 | 0.015968 | 475.013 | 0.01735 | 474.064 | 0.018645 | 494.894 | 0.019739 | 801.386 | 0.0177 | 1016.72 | 0.017023 | 1186 | 0.017878 | 1389 | 0.017385 | 2068.01 | 0.017524 | 2636.85 | 0.016787 | 2996.92 | 0.017878 | 3634.91 | 0.017298 | 3910.19 | 0.019897 | 3921.93 | 0.025472 | 4005.17 | 0.030587 | 4106.56 | 0.044997 | 4325.75 | 0.060315 | 5000.74 | 0.11201
456.845 | 0.016438 | 437.179 | 0.018167 | 445.12 | 0.019406 | 455.021 | 0.020897 | 737.557 | 0.018441 | 949.887 | 0.017577 | 1114.7 | 0.018386 | 1265.65 | 0.018058 | 1893.8 | 0.018294 | 2388.31 | 0.017524 | 2766.51 | 0.018571 | 3406.16 | 0.01786 | 3620.4 | 0.021107 | 3627.65 | 0.027511 | 3693.54 | 0.033434 | 3798.42 | 0.050279 | 4094.26 | 0.065798 | 4723.66 | 0.12454
422.988 | 0.016989 | 412.132 | 0.018908 | 415.027 | 0.02032 | 424.683 | 0.022012 | 688.381 | 0.019117 | 890.108 | 0.018112 | 1039.34 | 0.019175 | 1164.84 | 0.018833 | 1730.8 | 0.019329 | 2184.93 | 0.018331 | 2530.92 | 0.019542 | 3163.2 | 0.018608 | 3302.19 | 0.022956 | 3328.71 | 0.030132 | 3332.04 | 0.037773 | 3485.41 | 0.057145 | 3790.83 | 0.074783 | 4475.35 | 0.13819
385.424 | 0.017771 | 385.424 | 0.019818 | 378.927 | 0.021728 | 395.181 | 0.02342 | 642.485 | 0.019937 | 817.575 | 0.019041 | 974.908 | 0.020017 | 1070.99 | 0.019838 | 1596.13 | 0.020442 | 2029.08 | 0.019155 | 2355.1 | 0.020442 | 2973.04 | 0.019406 | 2996.92 | 0.025168 | 3075.86 | 0.032805 | 3039.17 | 0.042674 | 3269.33 | 0.063281 | 3495.88 | 0.085849 | 4172.79 | 0.158
356.147 | 0.018571 | 357.574 | 0.020938 | 351.547 | 0.023141 | 359.007 | 0.025549 | 601.45 | 0.020772 | 756.228 | 0.020097 | 914.468 | 0.020834 | 1004.59 | 0.020709 | 1463.14 | 0.021837 | 1888.13 | 0.020178 | 2211.31 | 0.021404 | 2758.22 | 0.020483 | 2642.13 | 0.028519 | 2797.1 | 0.036656 | 2830.87 | 0.047304 | 3017.97 | 0.071564 | 3204.59 | 0.099942 | 3921.93 | 0.17939
322.9 | 0.019858 | 332.401 | 0.022278 | 325.168 | 0.024794 | 323.87 | 0.028236 | 560.788 | 0.021858 | 691.832 | 0.021511 | 850.941 | 0.021968 | 935.745 | 0.021902 | 1358.78 | 0.023233 | 1755.2 | 0.021383 | 2055.63 | 0.022728 | 2528.4 | 0.021968 | 2397.88 | 0.031709 | 2595 | 0.040431 | 2658.03 | 0.051759 | 2791.52 | 0.081255 | 2934.64 | 0.1174 | 3671.44 | 0.20594
286.387 | 0.021728 | 308.692 | 0.023774 | 286.673 | 0.028067 | 293.637 | 0.031424 | 516.638 | 0.023397 | 638.641 | 0.022979 | 791.827 | 0.023233 | 875.104 | 0.023187 | 1243.07 | 0.025143 | 1651.34 | 0.022592 | 1912.83 | 0.02423 | 2345.7 | 0.023443 | 2220.17 | 0.034764 | 2383.54 | 0.045087 | 2503.24 | 0.056803 | 2574.32 | 0.093092 | 2736.24 | 0.13423 | 3412.98 | 0.23975
257.326 | 0.02375 | 285.243 | 0.025625 | 259.393 | 0.031205 | 269.17 | 0.034625 | 479.308 | 0.024968 | 581.344 | 0.025068 | 741.254 | 0.024547 | 807.016 | 0.025018 | 1130.41 | 0.027649 | 1525.9 | 0.024254 | 1788.87 | 0.025831 | 2161.03 | 0.025371 | 2031.11 | 0.038729 | 2209.1 | 0.050481 | 2341.02 | 0.063092 | 2421.98 | 0.10381 | 2530.92 | 0.1558 | 3188.61 | 0.27716
226.183 | 0.026751 | 261.215 | 0.027843 | 236.83 | 0.034418 | 241.132 | 0.039511 | 446.457 | 0.026832 | 525.496 | 0.027704 | 679.49 | 0.026751 | 736.083 | 0.027429 | 1024.89 | 0.030587 | 1391.78 | 0.026538 | 1674.62 | 0.027566 | 1937.86 | 0.028264 | 1856.3 | 0.043623 | 2029.08 | 0.057031 | 2193.69 | 0.070077 | 2271.83 | 0.11658 | 2355.1 | 0.18029 | 2999.92 | 0.31913
201.612 | 0.029952 | 244.776 | 0.029862 | 215.367 | 0.038613 | 222.148 | 0.043842 | 410.076 | 0.029183 | 473.117 | 0.030988 | 615.443 | 0.029535 | 673.402 | 0.030162 | 933.875 | 0.033906 | 1253.05 | 0.029565 | 1562.96 | 0.029565 | 1762.24 | 0.031362 | 1711.87 | 0.049038 | 1858.16 | 0.065535 | 2018.96 | 0.080125 | 2120.36 | 0.13237 | 2189.31 | 0.20968 | 2822.39 | 0.36672
178.992 | 0.034008 | 223.485 | 0.032937 | 191.587 | 0.045042 | 203.231 | 0.049679 | 375.532 | 0.032027 | 418.36 | 0.03529 | 559.668 | 0.032576 | 614.214 | 0.033468 | 858.634 | 0.037397 | 1134.94 | 0.033003 | 1405.77 | 0.033102 | 1615.4 | 0.034764 | 1585 | 0.055014 | 1689.76 | 0.076141 | 1845.19 | 0.093652 | 1978.99 | 0.1509 | 2018.96 | 0.24829 | 2674.03 | 0.41846
159.229 | 0.03904 | 204.659 | 0.036547 | 174.05 | 0.0515 | 184.813 | 0.057259 | 346.313 | 0.035219 | 382.353 | 0.039472 | 507.422 | 0.036547 | 566.991 | 0.03684 | 781.6 | 0.042292 | 1023.86 | 0.03736 | 1301.59 | 0.036219 | 1488.22 | 0.038497 | 1479.32 | 0.061044 | 1552.06 | 0.087583 | 1674.62 | 0.11123 | 1841.51 | 0.17322 | 1861.88 | 0.29636 | 2520.82 | 0.48376
142.5 | 0.044817 | 185.739 | 0.04133 | 156.701 | 0.060135 | 171.459 | 0.064689 | 316.19 | 0.039275 | 351.547 | 0.044062 | 460.054 | 0.041454 | 515.091 | 0.041704 | 723.675 | 0.047115 | 934.81 | 0.042039 | 1207.54 | 0.039709 | 1377.93 | 0.042759 | 1383.45 | 0.067734 | 1395.96 | 0.10465 | 1530.48 | 0.13131 | 1717.01 | 0.19946 | 1723.89 | 0.35093 | 2388.31 | 0.56205
127.656 | 0.051966 | 170.945 | 0.046228 | 141.082 | 0.071349 | 157.172 | 0.074484 | 289.554 | 0.044106 | 319.687 | 0.050229 | 417.107 | 0.047493 | 456.845 | 0.049234 | 660.068 | 0.053871 | 854.352 | 0.047636 | 1099.2 | 0.044997 | 1283.49 | 0.047304 | 1286.06 | 0.076217 | 1278.37 | 0.12231 | 1415.64 | 0.1515 | 1588.17 | 0.2329 | 1580.25 | 0.42521 | 2262.76 | 0.65301
112.995 | 0.061966 | 158.435 | 0.051243 | 129.068 | 0.082648 | 146.254 | 0.084149 | 265.428 | 0.049729 | 286.96 | 0.059062 | 380.446 | 0.054521 | 415.858 | 0.056689 | 617.293 | 0.059715 | 786.304 | 0.053656 | 1002.59 | 0.05109 | 1180.08 | 0.053656 | 1176.55 | 0.087759 | 1142.92 | 0.14999 | 1304.19 | 0.17637 | 1479.32 | 0.27032 | 1463.14 | 0.50653 | 2154.56 | 0.7534
97.7434 | 0.076446 | 144.654 | 0.058358 | 118.196 | 0.095736 | 129.456 | 0.1035 | 241.132 | 0.057145 | 255.02 | 0.070923 | 350.144 | 0.061966 | 372.167 | 0.067329 | 572.117 | 0.067329 | 725.124 | 0.060678 | 900.854 | 0.060015 | 1095.91 | 0.060075 | 1083.92 | 0.10115 | 1046.64 | 0.1769 | 1197.92 | 0.20718 | 1352 | 0.32558 | 1368.32 | 0.58969 | 2055.63 | 0.87009
85.9999 | 0.092628 | 135.686 | 0.064238 | 108.782 | 0.11056 | 119.145 | 0.12061 | 220.378 | 0.065535 | 230.752 | 0.083228 | 325.494 | 0.069657 | 334.068 | 0.080286 | 527.075 | 0.077215 | 671.385 | 0.068346 | 821.673 | 0.06931 | 1008.62 | 0.068415 | 1003.59 | 0.116 | 959.433 | 0.20947 | 1094.81 | 0.24606 | 1255.56 | 0.38245 | 1274.54 | 0.69687 | 1955.38 | 1.0058
76.7341 | 0.11145 | 126.513 | 0.071851 | 99.6183 | 0.13027 | 108.999 | 0.14253 | 201.209 | 0.075535 | 206.715 | 0.099842 | 299.569 | 0.079646 | 302.277 | 0.095353 | 481.229 | 0.08989 | 614.214 | 0.079011 | 759.259 | 0.078382 | 947.041 | 0.075837 | 935.745 | 0.13224 | 890.999 | 0.24289 | 1001.58 | 0.294 | 1173.02 | 0.44434 | 1193.13 | 0.81696 | 1865.6 | 1.1616
70.693 | 0.12871 | 117.02 | 0.080769 | 89.1523 | 0.16071 | 100.72 | 0.1666 | 182.974 | 0.087934 | 177.922 | 0.13027 | 273.511 | 0.093185 | 273.785 | 0.11325 | 442.457 | 0.10444 | 564.163 | 0.091066 | 694.605 | 0.090885 | 879.491 | 0.086107 | 867.264 | 0.15257 | 816.758 | 0.28992 | 909.907 | 0.35659 | 1089.35 | 0.52353 | 1134.94 | 0.92852 | 1783.51 | 1.3389
63.6466 | 0.15425 | 106.841 | 0.093559 | 78.598 | 0.20553 | 92.9764 | 0.19649 | 167.225 | 0.10247 | 151.463 | 0.17567 | 247.236 | 0.1119 | 245.757 | 0.13695 | 403.567 | 0.12317 | 514.576 | 0.10676 | 643.128 | 0.10392 | 814.311 | 0.098454 | 804.598 | 0.17514 | 753.963 | 0.34227 | 824.967 | 0.43511 | 1018.76 | 0.60462 | 1072.06 | 1.0702 | 1706.74 | 1.5447
57.2453 | 0.18523 | 97.2559 | 0.11056 | 71.8331 | 0.24435 | 85.828 | 0.23104 | 151.009 | 0.12256 | 133.132 | 0.22556 | 227.316 | 0.12988 | 224.83 | 0.16151 | 377.414 | 0.13943 | 475.013 | 0.12354 | 600.849 | 0.11728 | 741.995 | 0.11635 | 763.828 | 0.1924 | 683.58 | 0.4214 | 760.779 | 0.51574 | 947.041 | 0.71379 | 1025.91 | 1.2054 | 1638.18 | 1.7929
52.0053 | 0.22065 | 88.8852 | 0.12833 | 65.1926 | 0.29636 | 79.3085 | 0.26897 | 139.26 | 0.14168 | 120.102 | 0.27799 | 207.752 | 0.15257 | 202.015 | 0.19727 | 349.095 | 0.16135 | 443.786 | 0.13957 | 556.32 | 0.13464 | 680.851 | 0.13654 | 706.514 | 0.22243 | 622.873 | 0.51574 | 696.692 | 0.62553 | 883.016 | 0.83932 | 976.859 | 1.3783 | 1572.37 | 2.0665
47.2922 | 0.2618 | 78.9919 | 0.15784 | 60.3008 | 0.3464 | 72.5551 | 0.32041 | 128.81 | 0.16395 | 107.699 | 0.34605 | 190.822 | 0.1785 | 186.857 | 0.22897 | 322.255 | 0.18765 | 411.72 | 0.16087 | 524.446 | 0.15105 | 626.622 | 0.16055 | 650.241 | 0.25972 | 577.289 | 0.61069 | 650.241 | 0.73186 | 825.792 | 0.98693 | 936.681 | 1.554 | 1509.21 | 2.3913
42.8775 | 0.31375 | 72.4101 | 0.18394 | 56.2804 | 0.39766 | 66.843 | 0.37713 | 118.551 | 0.19163 | 98.7257 | 0.41389 | 175.624 | 0.20968 | 174.05 | 0.26154 | 296.884 | 0.21933 | 385.038 | 0.1832 | 478.829 | 0.18011 | 582.508 | 0.18523 | 589.54 | 0.31406 | 541.5 | 0.71095 | 607.494 | 0.85971 | 773.823 | 1.1663 | 890.108 | 1.82 | 1451.48 | 2.7645
38.488 | 0.38475 | 64.0937 | 0.23058 | 52.6331 | 0.45514 | 60.9069 | 0.45787 | 110.426 | 0.22021 | 90.3188 | 0.497 | 162.445 | 0.24508 | 161.151 | 0.30539 | 270.79 | 0.26233 | 360.086 | 0.20926 | 441.573 | 0.21116 | 538.799 | 0.21693 | 545.304 | 0.36452 | 509.966 | 0.81778 | 565.858 | 1.0241 | 734.612 | 1.3389 | 853.498 | 2.0831 | 1397.36 | 3.199
35.2811 | 0.45422 | 58.1105 | 0.27385 | 49.2715 | 0.5204 | 56.6757 | 0.53144 | 104.307 | 0.24804 | 83.2914 | 0.58851 | 150.106 | 0.28675 | 148.464 | 0.36198 | 250.722 | 0.30692 | 332.734 | 0.24435 | 405.996 | 0.25129 | 492.425 | 0.26024 | 490.46 | 0.45061 | 477.394 | 0.95584 | 533.438 | 1.1839 | 698.785 | 1.5447 | 820.852 | 2.3794 | 1345.26 | 3.713
31.3541 | 0.56149 | 50.7213 | 0.35058 | 45.7113 | 0.60947 | 53.2685 | 0.60765 | 96.8677 | 0.28789 | 77.2731 | 0.70317 | 140.378 | 0.32918 | 135.957 | 0.43467 | 231.677 | 0.36018 | 311.171 | 0.27938 | 369.202 | 0.30509 | 446.904 | 0.31627 | 446.457 | 0.54927 | 449.593 | 1.1172 | 508.947 | 1.3322 | 665.37 | 1.7768 | 792.619 | 2.7369 | 1302.89 | 4.2582
28.7416 | 0.66023 | 45.1661 | 0.43337 | 41.8188 | 0.7348 | 50.1163 | 0.69687 | 89.7785 | 0.33549 | 72.7731 | 0.81942 | 132.203 | 0.37338 | 124.879 | 0.52773 | 210.891 | 0.43816 | 288.687 | 0.32525 | 338.439 | 0.36452 | 406.809 | 0.38629 | 396.765 | 0.70811 | 419.617 | 1.3456 | 490.46 | 1.4723 | 634.821 | 2.0316 | 764.592 | 3.1482 | 1264.38 | 4.8688
25.8251 | 0.80964 | 40.7048 | 0.52879 | 39.3835 | 0.8318 | 46.7749 | 0.8137 | 82.6278 | 0.40005 | 68.6723 | 0.95013 | 125.254 | 0.4214 | 116.087 | 0.62678 | 194.483 | 0.52144 | 268.632 | 0.37826 | 311.794 | 0.43164 | 373.285 | 0.46248 | 357.217 | 0.8948 | 395.972 | 1.5918 | 474.539 | 1.6126 | 605.675 | 2.3393 | 732.412 | 3.8146 | 1233.16 | 5.4786
23.6023 | 0.96738 | 36.8312 | 0.642 | 37.09 | 0.95584 | 43.8312 | 0.95108 | 76.9646 | 0.46433 | 64.6731 | 1.115 | 118.196 | 0.47943 | 109.546 | 0.72603 | 177.034 | 0.642 | 248.724 | 0.4439 | 290.134 | 0.5035 | 347.354 | 0.54164 | 320.969 | 1.1524 | 376.284 | 1.8642 | 457.759 | 1.8001 | 586.6 | 2.6113 | 710.055 | 4.4364 | 1206.33 | 6.1524
21.1226 | 1.2175 | 33.0938 | 0.79679 | 34.9999 | 1.0962 | 41.0317 | 1.1139 | 71.618 | 0.54544 | 60.9678 | 1.3097 | 111.759 | 0.54599 | 102.652 | 0.85885 | 165.396 | 0.74964 | 233.304 | 0.50958 | 272.419 | 0.57743 | 323.547 | 0.63245 | 293.343 | 1.4533 | 356.503 | 2.223 | 442.9 | 2.0094 | 564.727 | 3.0248 | 684.263 | 5.3594 | 1175.37 | 6.9925
19.3626 | 1.4767 | 29.6466 | 1.0028 | 33.0938 | 1.2647 | 38.4111 | 1.3137 | 67.2452 | 0.63055 | 58.2851 | 1.5141 | 105.145 | 0.63435 | 96.8677 | 1.0069 | 155.142 | 0.87096 | 217.967 | 0.59324 | 252.735 | 0.68375 | 303.792 | 0.73113 | 273.785 | 1.7451 | 338.1 | 2.6747 | 428.094 | 2.2611 | 547.489 | 3.4655 | 665.37 | 6.2392 | 1145.2 | 7.9633
17.8561 | 1.7715 | 26.6648 | 1.2825 | 31.4798 | 1.4374 | 35.9578 | 1.5649 | 62.6364 | 0.74814 | 55.7761 | 1.7697 | 99.3199 | 0.73627 | 92.7906 | 1.1547 | 146.4 | 1.0139 | 204.659 | 0.68444 | 237.542 | 0.78887 | 286.1 | 0.84353 | 256.812 | 2.0935 | 317.457 | 3.3362 | 413.37 | 2.6061 | 529.717 | 4.0182 | 650.892 | 7.1624 | 1125.9 | 8.7657
16.5493 | 2.1294 | 24.5656 | 1.5525 | 29.6466 | 1.6885 | 33.9995 | 1.8218 | 58.9887 | 0.86922 | 53.6964 | 2.0768 | 93.4424 | 0.86488 | 89.7785 | 1.3071 | 138.012 | 1.1804 | 192.163 | 0.79044 | 220.378 | 0.94067 | 270.519 | 0.96545 | 240.409 | 2.5698 | 301.975 | 4.0749 | 400.352 | 2.9619 | 517.673 | 4.4765 | 634.186 | 8.5578 | 1104.71 | 9.7947
15.5078 | 2.524 | 23.2277 | 1.7929 | 28.032 | 1.9775 | 32.3737 | 2.0914 | 55.3871 | 1.0282 | 52.266 | 2.3961 | 88.7076 | 1.0069 | 86.604 | 1.5156 | 130.888 | 1.3605 | 179.53 | 0.93692 | 207.129 | 1.0962 | 249.721 | 1.1804 | 226.635 | 3.1419 | 285.529 | 5.1595 | 386.582 | 3.4378 | 505.902 | 5.0827 | 616.676 | 10.2969 | 1078.51 | 11.1545
14.7958 | 2.8946 | 22.0067 | 2.0562 | 26.3204 | 2.3841 | 31.1354 | 2.3699 | 52.3706 | 1.2006 | 50.8737 | 2.8401 | 84.6348 | 1.164 | 84.297 | 1.7226 | 124.754 | 1.5587 | 169.414 | 1.0885 | 194.288 | 1.2941 | 236.357 | 1.3659 | 214.507 | 3.7805 | 273.785 | 6.3334 | 372.167 | 4.0667 | 492.425 | 5.7825 | 605.675 | 11.5634 | 1059.27 | 12.5264
13.976 | 3.4551 | 20.8707 | 2.3818 | 24.8373 | 2.8316 | 29.8548 | 2.7178 | 50.1664 | 1.3564 | 49.6673 | 3.4207 | 80.8298 | 1.3564 | 82.1335 | 1.9618 | 119.026 | 1.8019 | 158.752 | 1.2993 | 183.157 | 1.5156 | 225.055 | 1.5618 | 203.434 | 4.6639 | 265.428 | 7.6358 | 361.529 | 4.6919 | 481.229 | 6.6848 | 596.061 | 13.2083 | 1038.3 | 14.1801
13.563 | 3.8491 | 19.9125 | 2.7452 | 23.6969 | 3.3196 | 28.9725 | 3.04 | 48.8301 | 1.4901 | 48.538 | 4.1282 | 77.8938 | 1.5556 | 80.1056 | 2.2679 | 114.588 | 2.0541 | 149.806 | 1.5293 | 173.876 | 1.7539 | 213.651 | 1.8109 | 195.262 | 5.6454 | 257.326 | 9.3357 | 350.845 | 5.4786 | 470.287 | 7.6511 | 587.774 | 15.1022 | 1019.78 | 16.0201
13.1227 | 4.4944 | 19.1126 | 3.1608 | 22.4737 | 4.0102 | 28.1162 | 3.4207 | 47.5293 | 1.6288 | 47.4343 | 5.1031 | 74.9893 | 1.8182 | 78.4409 | 2.6165 | 111.535 | 2.3369 | 142.358 | 1.7733 | 164.571 | 2.0603 | 203.842 | 2.0893 | 191.204 | 6.3018 | 251.726 | 10.9118 | 341.498 | 6.3652 | 460.054 | 8.7569 | 579.603 | 17.599 | 1003.59 | 17.8471
12.7094 | 5.3113 | 18.3815 | 3.6541 | 21.4633 | 4.7438 | 27.3946 | 3.8453 | 46.2632 | 1.8055 | 46.5416 | 6.208 | 72.9188 | 2.1145 | 76.5808 | 3.1325 | 108.673 | 2.6349 | 136.639 | 2.0195 | 157.644 | 2.3675 | 189.302 | 2.6454 | 187.044 | 7.1911 | 246.495 | 12.9467 | 333.4 | 7.3437 | 450.944 | 10.1842 | 571.545 | 20.3248 | 985.691 | 20.5086
12.4329 | 6.3018 | 17.8026 | 4.2582 | 20.6837 | 5.5558 | 26.8253 | 4.3225 | 45.3018 | 1.9954 | 45.6656 | 7.9394 | 71.1895 | 2.4666 | 74.9893 | 3.6945 | 106.734 | 2.9207 | 131.807 | 2.2861 | 152.222 | 2.6694 | 183.34 | 2.956 | 182.426 | 8.3465 | 240.169 | 16.1973 | 326.145 | 8.4557 | 442.9 | 11.7852 | 564.727 | 23.4729 | 971.016 | 23.0772
12.2233 | 7.4622 | 17.3284 | 4.9424 | 19.9723 | 6.752 | 26.163 | 5.0827 | 44.1391 | 2.2792 | 45.1209 | 9.8242 | 69.5013 | 2.9383 | 73.5044 | 4.472 | 104.516 | 3.3396 | 127.656 | 2.5879 | 149.059 | 2.9033 | 179.351 | 3.2702 | 177.922 | 9.8045 | 235.885 | 19.4111 | 318.411 | 9.9328 | 436.742 | 13.5833 | 559.108 | 27.1627 | 954.648 | 26.1238
12.0293 | 9.0326 | 16.9683 | 5.725 | 19.4987 | 8.1323 | 25.7735 | 5.7883 | 43.0924 | 2.5957 | 44.5381 | 12.6271 | 67.8532 | 3.5997 | 72.2654 | 5.2901 | 102.447 | 3.7805 | 124.38 | 2.8801 | 145.524 | 3.2086 | 175.799 | 3.5925 | 174.748 | 11.2891 | 230.983 | 25.4024 | 311.794 | 11.5865 | 430.24 | 15.8607 | 553.545 | 31.3385 | 939.495 | 29.1031
11.8621 | 10.7708 | 16.6323 | 6.6316 | 19.2084 | 9.4484 | 25.4406 | 6.6449 | 41.9025 | 3.0736 | 44.1833 | 15.6089 | 66.7094 | 4.2158 | 70.9763 | 6.4099 | 100.619 | 4.366 | 121.43 | 3.2604 | 142.073 | 3.5674 | 172.146 | 3.9942 | 171.459 | 13.103 | 227.089 | 31.4326 | 305.62 | 13.4482 | 423.411 | 18.299 | 550.784 | 34.8777 | 922.736 | 32.0997
11.6971 | 13.3543 | 16.2866 | 7.9474 | 18.9035 | 11.8088 | 25.2127 | 7.6358 | 41.0728 | 3.5354 | 43.8312 | 19.6651 | 65.5849 | 5.002 | 70.1998 | 7.4027 | 98.8245 | 5.0827 | 119.145 | 3.665 | 138.704 | 3.9703 | 169.075 | 4.4231 | 168.569 | 15.2235 | 223.261 | 41.0113 | 299.569 | 15.6245 | 413.784 | 21.8859 | 544.214 | 39.8789 | 908.998 | 35.1227
11.5692 | 17.0618 | 16.0602 | 9.2428 | 18.6593 | 15.3152 | 24.9618 | 8.7657 | 40.2193 | 4.2285 | 43.5255 | 24.9992 | 64.6085 | 6.0306 | 69.1547 | 9.087 | 97.2559 | 5.9765 | 117.254 | 4.0953 | 135.009 | 4.4989 | 165.066 | 5.175 | 166.391 | 17.2333 | 219.718 | 53.8848 | 294.814 | 18.0265 | 406.402 | 25.1748 | 537.723 | 45.2792 | 883.016 | 40.5626
11.5 | 21.6033 | 15.8211 | 10.8682 | 18.5292 | 18.9887 | 24.7381 | 10.1537 | 39.6205 | 4.8981 | 43.3517 | 29.6614 | 63.8378 | 7.1338 | 68.3298 | 10.89 | 95.808 | 7.1767 | 114.932 | 4.6732 | 132.203 | 5.0171 | 161.959 | 5.9646 | 164.407 | 19.8429 | 217.097 | 70.0247 | 289.844 | 20.9858 | 399.152 | 29.016 | 532.372 | 50.0413 | 858.634 | 46.4719
11.4198 | 27.5181 | 15.6168 | 12.6397 | 18.5106 | 24.4308 | 24.6394 | 11.7381 | 39.1479 | 5.6511 | 43.1355 | 36.8865 | 63.0764 | 8.4136 | 67.5147 | 13.1819 | 93.817 | 9.0146 | 112.431 | 5.5226 | 129.845 | 5.6004 | 158.911 | 6.8541 | 161.635 | 24.701 | 215.367 | 86.9079 | 286.1 | 24.2119 | 393.21 | 33.3096 | 526.548 | 55.0834 | 836.597 | 53.616
11.3855 | 35.2987 | 15.4614 | 14.6706 | 18.4552 | 32.1318 | 24.6148 | 13.8439 | 38.6809 | 6.5198 | 42.9203 | 47.4107 | 62.324 | 10.1639 | 66.5761 | 16.9767 | 92.2356 | 11.2104 | 110.205 | 6.5133 | 127.784 | 6.2956 | 156.232 | 7.8213 | 160.027 | 28.8424 | 212.798 | 113.391 | 281.841 | 28.7272 | 386.968 | 38.1622 | 519.228 | 61.5499 | 815.942 | 61.1206
11.2948 | 45.0984 | 15.3229 | 17.3024 | 18.4367 | 43.941 | 24.6394 | 15.829 | 38.296 | 7.6434 | 42.7918 | 63.9338 | 61.519 | 12.9467 | 65.9796 | 20.5086 | 90.7715 | 14.612 | 108.673 | 7.4771 | 126.008 | 7.1053 | 153.752 | 8.9428 | 157.802 | 37.0344 | 210.47 | 143.861 | 276.537 | 34.9475 | 381.589 | 43.6781 | 508.947 | 70.0247 | 795.796 | 68.9133
11.216 | 56.5343 | 15.2008 | 21.0699 | 18.4183 | 55.6926 | 24.6148 | 18.7247 | 37.9529 | 9.1692 | 42.5784 | 86.1293 | 61.0288 | 15.4846 | 65.5194 | 25.1748 | 89.7785 | 17.599 | 106.948 | 8.722 | 124.256 | 8.3465 | 151.463 | 10.266 | 156.388 | 46.4719 | 207.959 | 181.971 | 272.147 | 42.3449 | 376.284 | 49.9413 | 500.868 | 77.1575 | 776.924 | 76.161
11.1713 | 68.5696 | 15.0646 | 26.5982 | 18.3815 | 69.1895 | 24.5901 | 21.6682 | 37.6882 | 11.1545 | 42.4933 | 114.99 | 60.3612 | 19.7044 | 65.1274 | 30.8719 | 88.5304 | 22.2389 | 105.567 | 10.2763 | 122.651 | 9.6104 | 149.208 | 11.9155 | 155.297 | 59.1365 | 206.096 | 228.8 | 268.632 | 50.5442 | 371.052 | 56.7042 | 492.425 | 85.614 | 753.209 | 86.561
11.1267 | 82.0107 | 14.9147 | 33.4431 | 18.3815 | 85.8713 | 24.541 | 24.382 | 37.3879 | 13.7473 | 42.3237 | 148.688 | 59.9401 | 23.995 | 64.6731 | 37.8582 | 87.6495 | 27.8504 | 104.099 | 12.2539 | 121.188 | 11.0877 | 146.254 | 14.7441 | 154.368 | 77.0804 | 204.25 | 272.83 | 265.428 | 61.4884 | 366.26 | 65.095 | 484.609 | 94.4291 | 735.347 | 97.5973
11.0712 | 102.601 | 14.8551 | 41.2168 | 18.3815 | 107.538 | 24.541 | 28.018 | 37.1271 | 16.8078 | 42.2391 | 180.341 | 59.4625 | 29.4545 | 64.3506 | 46.8451 | 86.7774 | 35.0525 | 102.754 | 14.6706 | 119.503 | 13.1951 | 144.365 | 17.3717 | 153.445 | 98.3812 | 203.638 | 297.928 | 262 | 74.058 | 360.086 | 76.6193 | 475.489 | 106.255 | 718.627 | 109.491
10.983 | 122.836 | 14.7663 | 52.8706 | 18.3631 | 131.348 | 24.541 | 33.8807 | 36.8312 | 20.1427 | 42.0705 | 220.931 | 59.2251 | 36.556 | 63.9017 | 58.3727 | 86.0859 | 43.941 | 101.63 | 17.5814 | 118.078 | 15.7029 | 142.785 | 20.1629 | 152.985 | 126.071 |  |  | 258.874 | 89.2864 | 354.371 | 88.2214 | 467.941 | 117.313 | 697.389 | 128.876
10.9391 | 147.208 | 14.6779 | 66.1449 | 18.3631 | 179.621 | 24.5901 | 39.6403 | 36.5743 | 24.7505 | 42.0284 | 263.71 | 58.8708 | 44.9184 | 63.583 | 71.083 | 85.3146 | 57.7341 | 100.619 | 21.0699 | 117.02 | 18.894 | 141.223 | 23.1234 | 152.527 | 154.756 |  |  | 255.275 | 114.646 | 348.049 | 100.77 | 457.759 | 131.874 | 680.17 | 149.582
10.8737 | 192.838 | 14.6486 | 80.5477 | 18.3815 | 214.616 | 24.541 | 45.8717 | 36.3919 | 29.6614 | 41.9864 | 304.555 | 58.5772 | 55.637 | 63.2026 | 87.5184 | 84.7195 | 71.654 | 99.8177 | 25.5043 | 115.739 | 23.1697 | 139.539 | 27.2443 | 151.918 | 199.707 |  |  | 252.735 | 137.256 | 341.498 | 115.914 | 447.798 | 147.798 | 664.04 | 172.751
10.8303 | 242.221 | 14.5901 | 98.8743 | 18.3815 | 248.353 | 24.492 | 53.6697 | 36.2104 | 37.0714 |  |  | 58.1686 | 70.1649 | 62.8874 | 106.575 | 84.3813 | 89.4652 | 98.9234 | 30.841 | 114.702 | 27.962 | 137.874 | 32.0676 | 151.463 | 248.85 |  |  | 250.722 | 163.669 | 335.071 | 135.077 | 434.999 | 170.008 | 652.847 | 190.919
10.8194 | 273.924 | 14.5464 | 119.324 | 18.3815 | 280.017 | 24.492 | 62.7305 | 36.1742 | 44.6051 |  |  | 57.8785 | 85.9572 | 62.5112 | 131.348 | 84.0444 | 112.6 | 98.3316 | 37.2945 | 113.789 | 33.813 | 136.639 | 37.3318 | 151.161 | 298.524 |  |  | 249.222 | 190.919 | 329.423 | 153.523 | 422.143 | 195.556 | 638.003 | 213.545
10.7762 | 306.388 | 14.4884 | 147.65 | 18.3999 | 301.524 | 24.443 | 77.312 | 36.1019 | 55.2489 |  |  | 57.6474 | 106.468 | 62.324 | 164.161 | 83.7089 | 138.913 | 97.5481 | 46.4254 | 113.108 | 41.2581 | 135.55 | 43.7218 |  |  |  |  | 247.236 | 238.615 | 322.9 | 176.593 | 410.487 | 223.598 | 624.12 | 232.723
|  | 14.4305 | 181.789 |  |  | 24.443 | 90.9991 | 36.0298 | 70.7285 |  |  | 57.3599 | 131.479 | 62.0752 | 209.736 | 83.3748 | 167.143 | 96.9646 | 55.2489 | 112.431 | 48.9524 | 134.47 | 51.3081 |  |  |  |  | 246.249 | 270.657 | 315.558 | 204.967 | 398.355 | 254.131 | 602.654 | 263.447
|  | 14.3729 | 219.17 |  |  | 24.4675 | 111.035 | 35.886 | 86.9949 |  |  | 57.1309 | 165.48 | 61.8274 | 254.385 | 83.2914 | 202.928 | 96.3845 | 69.0512 | 111.759 | 59.3142 | 133.399 | 58.6066 |  |  |  |  | 245.757 | 300.922 | 309.001 | 231.563 | 388.908 | 286.532 | 583.674 | 294.374
|  | 14.3012 | 261.086 |  |  | 24.4675 | 131.479 | 35.7785 | 109.601 |  |  | 56.7892 | 204.149 | 61.6422 | 304.555 | 83.0419 | 251.854 | 95.808 | 84.9319 | 111.201 | 73.615 | 132.601 | 69.3973 | [6 empty] | 303.792 | 254.64 | 381.97 | 321.775 | 567.558 | 320.17
|  | 14.2441 | 307.923 |  |  | 24.4675 | 157.409 | 35.707 | 133.199 |  |  | 56.5625 | 252.106 |  |  | 82.876 | 306.081 | 95.0445 | 108.51 | 110.426 | 89.6443 | 131.939 | 79.9858 | [6 empty] | 299.868 | 270.927 | 374.781 | 367.18 | 552.992 | 348.226
[6 empty] | 24.492 | 185.091 | 35.707 | 170.179 |  |  | 56.3931 | 304.555 |  |  |  |  | 94.5705 | 134.404 | 109.546 | 111.035 | 131.15 | 97.0134 | [6 empty] | 295.699 | 289.701 | 370.311 | 407.016 | 537.723 | 389.106
[6 empty] | 24.492 | 217.424 | 35.6713 | 216.99 | [8 empty] | 94.0988 | 164.819 | 109.108 | 131.611 | 130.626 | 115.682 | [6 empty] | 292.464 | 311.018 | 367.36 | 455.253 | 526.548 | 422.78
[6 empty] | 24.492 | 253.117 | 35.6356 | 255.916 | [8 empty] | 93.5359 | 197.917 | 108.347 | 168.485 | 129.845 | 139.889 | [6 empty] | 289.265 | 337.259 | 364.433 | 502.629 | 516.638 | 460.288
[6 empty] | 24.5165 | 299.421 | 35.7427 | 299.122 | [8 empty] | 93.1625 | 239.332 | 107.807 | 203.537 | 129.197 | 164.161 | [6 empty] | 286.96 | 358.114 | 363.342 | 561.636 | 506.408 | 510.226
[18 empty] | 92.8835 | 276.4 | 107.269 | 249.598 | 128.682 | 193.224 | [6 empty] | 283.537 | 391.448 | 362.616 | 606.59 | 499.368 | 547.221
[18 empty] | 92.7906 | 303.642 | 106.841 | 303.036 | 127.912 | 232.491 | [6 empty] | 279.875 | 433.05 |  |  | 495.389 | 577.584
[22 empty] | 127.274 | 273.377 | [6 empty] | 276.813 | 477.16 |  |  | 493.411 | 593.985
[22 empty] | 126.766 | 301.524 | [6 empty] | 274.608 | 516.902
[30 empty] | 272.965 | 553.274
[30 empty] | 271.332 | 601.155