## 176_16
S&C Power Fuses - Types SMD-2B and SMD- 3 (69 kV) | [9 empty] | S&C Power Fuses - Types SMD-2B and SMD- 3 (69 kV) | [9 empty] | S&C Power Fuses - Types SMD-2B and SMD- 3 (69 kV)
Very Slow Speed (TCC 176-1-6) | [9 empty] | Very Slow Speed (TCC 176-1-6) | [9 empty] | Very Slow Speed (TCC 176-1-6)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25007.4 | 0.030404 | 25007.4 | 0.030618 | 25007.4 | 0.030771 | 25007.4 | 0.031487 | 25005.7 | 0.033398 | 25005.7 | 0.034447 | 25005.7 | 0.035165 | 25005.7 | 0.036352 | 25005.7 | 0.039117 | 25005.7 | 0.046768 | 25005.7 | 0.051846 | 24991.4 | 0.065415
22923.7 | 0.030895 | 22514.7 | 0.031174 | 22537.3 | 0.031582 | 22201.7 | 0.032511 | 22159.2 | 0.034506 | 22868.4 | 0.03559 | 23052.5 | 0.036415 | 23492.3 | 0.037494 | 23573.2 | 0.040437 | 23026.1 | 0.05073 | 22045.3 | 0.059415 | 22299.2 | 0.075353
21502.5 | 0.031299 | 21097.8 | 0.031677 | 21118.9 | 0.032091 | 20783.7 | 0.033102 | 18735.8 | 0.036415 | 20276.8 | 0.037537 | 20230.4 | 0.038693 | 20806.2 | 0.039954 | 21337.2 | 0.043763 | 20057.3 | 0.058672 | 18543.6 | 0.072268 | 19093.3 | 0.093029
20068.9 | 0.031804 | 19651.8 | 0.032188 | 19691.2 | 0.032609 | 19359.2 | 0.033906 | 16180.5 | 0.038384 | 16823.2 | 0.040997 | 17551.5 | 0.041707 | 18406.1 | 0.042845 | 18692.9 | 0.048514 | 17743.6 | 0.066701 | 15741.8 | 0.088457 | 17065.8 | 0.10883
18637.4 | 0.032285 | 18231.8 | 0.032707 | 18250.1 | 0.033301 | 17924.5 | 0.034695 | 13965.8 | 0.041068 | 14412.7 | 0.044597 | 15045.4 | 0.045683 | 16442.1 | 0.045866 | 15262.3 | 0.058037 | 15850.3 | 0.076003 | 13783 | 0.10619 | 15045.4 | 0.13132
17204.5 | 0.032904 | 16796.5 | 0.033401 | 16830.1 | 0.034008 | 16496.8 | 0.03568 | 12006 | 0.044292 | 12525.8 | 0.048237 | 13226.2 | 0.049866 | 14371.5 | 0.050614 | 13325 | 0.065904 | 13501.7 | 0.093777 | 11713.9 | 0.13459 | 13015.8 | 0.16455
15786.7 | 0.033501 | 15366.2 | 0.03411 | 15396.9 | 0.034799 | 15061.9 | 0.036877 | 10506.1 | 0.047633 | 10731.1 | 0.053658 | 11448.6 | 0.055788 | 12911.8 | 0.055121 | 11292.3 | 0.079157 | 11660.3 | 0.11492 | 10285.8 | 0.1655 | 11547.4 | 0.20038
14356 | 0.034212 | 13931.7 | 0.035008 | 13973.6 | 0.035895 | 13628.6 | 0.038305 | 9310.15 | 0.051905 | 9078.45 | 0.06181 | 9853.31 | 0.06419 | 11488 | 0.061176 | 10064.3 | 0.091131 | 9978.25 | 0.14533 | 9005.95 | 0.20643 | 10274 | 0.24512
12925.1 | 0.035114 | 12505.5 | 0.036002 | 12543.1 | 0.037099 | 12196.7 | 0.040229 | 8350.17 | 0.056593 | 7697.92 | 0.072475 | 8647.06 | 0.073394 | 10268.1 | 0.068874 | 8817.1 | 0.10858 | 8514.37 | 0.18696 | 8017.41 | 0.25297 | 9114.92 | 0.30349
11497.9 | 0.036075 | 11080.3 | 0.037285 | 11102.5 | 0.03869 | 10774.4 | 0.042589 | 7497.76 | 0.062272 | 6655.68 | 0.085567 | 7597.18 | 0.085323 | 9214.66 | 0.077497 | 7782.15 | 0.12901 | 7232.03 | 0.2447 | 7088.5 | 0.31195 | 8137.7 | 0.37404
10066 | 0.037397 | 9652.07 | 0.038923 | 9681.07 | 0.040837 | 9338.75 | 0.045998 | 6591.19 | 0.070591 | 5728.24 | 0.10301 | 6763.28 | 0.098342 | 8058.85 | 0.091078 | 6572.34 | 0.16712 | 6372.18 | 0.30558 | 6383.14 | 0.38095 | 7408.11 | 0.44746
8629.38 | 0.039118 | 8216.73 | 0.041124 | 8249.67 | 0.043711 | 8999.53 | 0.047115 | 5877.8 | 0.080298 | 5006.87 | 0.12295 | 6007.13 | 0.11498 | 7088.5 | 0.10729 | 5741.38 | 0.2075 | 5534.74 | 0.39314 | 5794.24 | 0.45339 | 6640.45 | 0.55368
7200.66 | 0.041371 | 6788.11 | 0.044415 | 6815.32 | 0.048163 | 8492.41 | 0.048891 | 5259.67 | 0.091078 | 4353.85 | 0.15015 | 5384.65 | 0.13413 | 6206.49 | 0.12864 | 5001.14 | 0.26166 | 4964.04 | 0.48121 | 5181.93 | 0.55942 | 5884.54 | 0.70341
5772.89 | 0.044997 | 5355.76 | 0.049878 | 6660.36 | 0.048793 | 7894.55 | 0.051192 | 4703.85 | 0.10444 | 3836.19 | 0.18368 | 4848.83 | 0.1562 | 5518.91 | 0.15336 | 4331.46 | 0.33644 | 4424.23 | 0.5999 | 4618.42 | 0.6966 | 5232.63 | 0.89568
4341.3 | 0.0515 | 5223.53 | 0.050683 | 6418.43 | 0.049878 | 7243.99 | 0.054412 | 4264.99 | 0.11859 | 3426.87 | 0.21973 | 4294.41 | 0.18858 | 4871.1 | 0.18632 | 3902.68 | 0.40572 | 3958.96 | 0.74274 | 4034.5 | 0.90704 | 4736.29 | 1.0907
4251.08 | 0.052018 | 5008.68 | 0.051914 | 6093.2 | 0.051603 | 6707.14 | 0.057777 | 3829.61 | 0.13755 | 3055.97 | 0.26634 | 3875.95 | 0.22277 | 4316.6 | 0.22559 | 3492.26 | 0.50434 | 3538.57 | 0.92328 | 3658.09 | 1.1007 | 4226.09 | 1.3801
4137.84 | 0.052804 | 4717 | 0.053817 | 5726.89 | 0.053602 | 6081.02 | 0.062714 | 3460.4 | 0.1589 | 2740.87 | 0.32359 | 3581.39 | 0.25486 | 3898.21 | 0.26818 | 3094.72 | 0.63634 | 3125 | 1.1783 | 3332.04 | 1.3228 | 3747.16 | 1.7644
3983.55 | 0.053925 | 4442.3 | 0.055957 | 5350.41 | 0.056182 | 5574.33 | 0.06787 | 3101.82 | 0.18782 | 2461.07 | 0.39269 | 3243.54 | 0.30124 | 3554.82 | 0.31464 | 2797.97 | 0.77755 | 2770.86 | 1.5013 | 2925.8 | 1.7353 | 3360.79 | 2.2338
3759.08 | 0.055901 | 4117.2 | 0.058885 | 4939.05 | 0.059596 | 5069.15 | 0.074559 | 2836.69 | 0.21623 | 2185.92 | 0.48983 | 2986.75 | 0.349 | 3155.58 | 0.38933 | 2547.11 | 0.93874 | 2454.03 | 1.9437 | 2569.09 | 2.3172 | 3024.63 | 2.8169
3518.99 | 0.058299 | 3831.18 | 0.06209 | 4541.12 | 0.063726 | 4674.74 | 0.081336 | 2558.81 | 0.25632 | 1988.8 | 0.58867 | 2745.58 | 0.40665 | 2867.73 | 0.46682 | 2321.41 | 1.134 | 2187.17 | 2.5034 | 2357.59 | 2.804 | 2777.21 | 3.4223
3297.53 | 0.060922 | 3501.44 | 0.066592 | 4217.21 | 0.06787 | 4183.6 | 0.091982 | 2322.74 | 0.3009 | 1798.09 | 0.71806 | 2560.28 | 0.46257 | 2618.11 | 0.55368 | 2089.21 | 1.4096 | 1948.21 | 3.256 | 2135.18 | 3.5358 | 2534.02 | 4.2983
3083.83 | 0.063917 | 3190.49 | 0.072283 | 3892.97 | 0.072937 | 3858.09 | 0.10125 | 2094.01 | 0.35996 | 1662.39 | 0.84583 | 2352.19 | 0.54519 | 2348.16 | 0.68552 | 1905.18 | 1.7058 | 1766.45 | 4.1223 | 1940.42 | 4.4587 | 2316.1 | 5.3984
2849.58 | 0.06787 | 2907.15 | 0.078696 | 3666.26 | 0.077292 | 3579.32 | 0.11134 | 1886.72 | 0.43358 | 1524.66 | 1.0084 | 2161.02 | 0.6411 | 2137.63 | 0.8182 | 1708.73 | 2.1473 | 1593.41 | 5.3156 | 1737.35 | 5.9198 | 2122.99 | 6.7841
2648.98 | 0.072139 | 2635.76 | 0.086972 | 3459.67 | 0.082071 | 3307.43 | 0.12391 | 1716.58 | 0.51485 | 1389.56 | 1.2209 | 2009.41 | 0.74487 | 1920.51 | 1.0153 | 1546.65 | 2.6754 | 1429.11 | 7.1429 | 1554.64 | 8.028 | 1972.92 | 8.3563
2460.03 | 0.076983 | 2416.14 | 0.095544 | 3168.23 | 0.09007 | 2998.68 | 0.14211 | 1560 | 0.61661 | 1254.16 | 1.5099 | 1867.36 | 0.86 | 1754.35 | 1.2112 | 1365.1 | 3.5399 | 1325.05 | 8.864 | 1452.21 | 9.9966 | 1825.07 | 10.5312
2300.61 | 0.081989 | 2170.97 | 0.10837 | 2858.15 | 0.10135 | 2784.79 | 0.15879 | 1455.54 | 0.70341 | 1135.84 | 1.8577 | 1731.39 | 1.0015 | 1570.75 | 1.516 | 1256.31 | 4.3131 | 1231.38 | 11.0882 | 1364.32 | 12.505 | 1678.66 | 14.0223
2132.24 | 0.088375 | 2004.05 | 0.11989 | 2586.16 | 0.11508 | 2534.95 | 0.18412 | 1343.39 | 0.81914 | 1020.48 | 2.352 | 1602.56 | 1.1649 | 1425.02 | 1.8662 | 1137.8 | 5.5489 | 1134.54 | 14.5708 | 1292.07 | 15.5092 | 1601.64 | 16.5743
1990.08 | 0.095068 | 1826.08 | 0.13518 | 2309.83 | 0.13303 | 2309.83 | 0.21328 | 1213.87 | 0.99292 | 941.309 | 2.8185 | 1471.47 | 1.3904 | 1309.2 | 2.2262 | 1040.54 | 7.0333 | 1054.95 | 19.9873 | 1215.26 | 19.6807 | 1511.62 | 21.1289
1806.1 | 0.10602 | 1699.23 | 0.14895 | 2081.67 | 0.15425 | 2100.49 | 0.24978 | 1103.15 | 1.2049 | 854.466 | 3.5278 | 1360.42 | 1.6331 | 1213.87 | 2.6118 | 957.623 | 9.0279 | 1007.7 | 25.5236 | 1157.52 | 25.0459 | 1450.55 | 26.1749
1640.78 | 0.11894 | 1592.29 | 0.16281 | 1896.81 | 0.1769 | 1937.06 | 0.28789 | 1008.85 | 1.4291 | 791.34 | 4.2348 | 1242.72 | 1.9694 | 1116.49 | 3.1605 | 887.384 | 11.5549 | 962.572 | 34.5142 | 1115.85 | 32.0383 | 1388.76 | 34.3958
1471.34 | 0.13654 | 1468.4 | 0.18394 | 1719.74 | 0.20491 | 1777.44 | 0.33515 | 906.91 | 1.7654 | 723.286 | 5.2521 | 1146.96 | 2.3506 | 1030.46 | 3.8375 | 829.392 | 14.5791 | 931.655 | 46.4318 | 1085.59 | 42.1008 | 1350.33 | 42.8794
1333.99 | 0.15643 | 1358.22 | 0.20718 | 1584.35 | 0.2336 | 1629.34 | 0.39174 | 834.634 | 2.0951 | 659.572 | 6.7415 | 1074.46 | 2.7077 | 952.7 | 4.6704 | 779.196 | 18.628 | 906.91 | 62.3572 | 1056.16 | 55.897 | 1311.46 | 56.9307
1224.06 | 0.17637 | 1241.32 | 0.23855 | 1447.98 | 0.27032 | 1492.08 | 0.45925 | 743.021 | 2.7031 | 612.245 | 8.2943 | 983.189 | 3.3295 | 883.834 | 5.658 | 729.527 | 25.1321 | 888.91 | 82.2714 | 1036.38 | 73.8326 | 1279.55 | 75.1118
1140.16 | 0.19629 | 1160.87 | 0.26656 | 1326.01 | 0.31344 | 1342.01 | 0.56037 | 683.806 | 3.2448 | 569.292 | 10.3104 | 903.281 | 4.0313 | 829.867 | 6.757 | 696.854 | 32.9122 | 876.775 | 106.391 | 1015.23 | 100.816 | 1259.19 | 94.7163
1049.35 | 0.22265 | 1079.15 | 0.29994 | 1193.84 | 0.37563 | 1222.83 | 0.66887 | 637.291 | 3.8069 | 531.174 | 12.9569 | 834.634 | 4.923 | 769.88 | 8.4139 | 670.235 | 43.6473 | 868.777 | 142.066 | 1004.82 | 135.627 | 1244.85 | 119.574
958.08 | 0.25662 | 992.206 | 0.34605 | 1103.15 | 0.43294 | 1087.82 | 0.82848 | 583.487 | 4.6784 | 499.027 | 16.5553 | 777.858 | 5.8894 | 727.441 | 10.2281 | 649.823 | 58.183 | 863.32 | 187.651 | 993.946 | 187.329 | 1234.91 | 148.981
869.511 | 0.30084 | 912.265 | 0.40045 | 1010.22 | 0.50603 | 991.214 | 0.99485 | 538.835 | 5.756 | 475.042 | 20.7215 | 717.51 | 7.3 | 696.854 | 11.8633 | 633.288 | 77.6483 | 859.374 | 240.177 | 987.138 | 239.217 | 1222.94 | 198.709
809.916 | 0.33886 | 829.589 | 0.47513 | 922.356 | 0.59621 | 904.092 | 1.1922 | 497.315 | 7.1839 | 451.175 | 26.4007 | 662.981 | 9.2053 | 673.313 | 13.4714 | 621.431 | 101.744 | 858.882 | 330.028 | 986.008 | 294.148 | 1217.35 | 263.976
740.948 | 0.39449 | 767.341 | 0.54599 | 862.583 | 0.67695 | 812.35 | 1.4886 | 451.175 | 9.7255 | 428.262 | 35.072 | 625.717 | 11.12 | 646.482 | 15.7689 | 612.245 | 140.047 | 858.39 | 411.428 | 979.816 | 394.584 | 1213.87 | 330.028
673.125 | 0.46572 | 699.895 | 0.64716 | 804.267 | 0.77557 | 743.175 | 1.7911 | 422.415 | 12.2218 | 414.269 | 43.6473 | 588.184 | 13.9582 | 618.944 | 18.8534 | 606.313 | 189.486 | 856.916 | 518.218 | 975.895 | 492.188 | 1209.02 | 438.93
619.511 | 0.53893 | 625.738 | 0.7952 | 748.395 | 0.89301 | 678.532 | 2.1833 | 400.733 | 14.8232 | 394.583 | 61.2601 | 559.594 | 17.1831 | 592.92 | 23.1561 | 604.926 | 242.666 | 859.374 | 594.902 | 974.22 | 576.128 | 1206.94 | 540.339
575.898 | 0.61437 | 558.878 | 0.9889 | 697.799 | 1.0262 | 632.026 | 2.5494 | 378.426 | 18.8318 | 382.347 | 86.0292 | 532.088 | 21.78 | 572.89 | 28.3596 | 603.196 | 319.613 |  |  | 970.878 | 597.291 | 1206.94 | 598.318
527.913 | 0.72025 | 510.265 | 1.1792 | 648.026 | 1.1887 | 582.851 | 3.043 | 360.031 | 24.117 | 375.188 | 110.552 | 510.299 | 26.4612 | 554.489 | 35.7206 | 603.541 | 415.928
492.715 | 0.81942 | 468.685 | 1.3991 | 606.031 | 1.3605 | 542.361 | 3.5925 | 347.47 | 30.0309 | 370.49 | 136.172 | 494.475 | 31.134 | 536.986 | 47.8077 | 603.541 | 511.731
458.487 | 0.93879 | 427.063 | 1.697 | 569.029 | 1.554 | 508.737 | 4.1864 | 335.732 | 39.5082 | 366.271 | 177.817 | 478.866 | 37.6528 | 523.923 | 62.2502 | 603.887 | 590.49
420.284 | 1.1127 | 393.441 | 2.0114 | 534.82 | 1.7733 | 475.293 | 4.9374 | 325.507 | 52.4848 | 364.179 | 229.686 | 461.366 | 49.5639 | 509.715 | 87.0201
384.495 | 1.3242 | 362.104 | 2.3985 | 501.163 | 2.0418 | 443.16 | 5.9112 | 319.962 | 65.9943 | 363.345 | 303.733 | 450.142 | 64.0582 | 501.319 | 116.733
349.999 | 1.5981 | 332.264 | 2.9033 | 466.814 | 2.3937 | 416.519 | 7.0206 | 313.791 | 83.7928 | 363.762 | 391.21 | 444.251 | 79.3564 | 495.609 | 149.237
323.737 | 1.8811 | 306.412 | 3.5003 | 442.717 | 2.6962 | 387.583 | 8.5493 | 310.395 | 105.3 | 363.97 | 487.42 | 438.187 | 102.27 | 493.061 | 185.833
306.106 | 2.1124 | 284.556 | 4.1655 | 419.025 | 3.0705 | 367.209 | 10.0527 | 306.86 | 135.938 | 364.596 | 561.151 | 433.941 | 127.057 | 490.245 | 236.493
283.42 | 2.474 | 269.328 | 4.7676 | 398.191 | 3.4724 | 346.863 | 12.0956 | 304.409 | 176.397 | 364.805 | 595.583 | 430.229 | 170.831 | 489.683 | 305.477
260.586 | 2.9738 | 255.681 | 5.4349 | 379.15 | 3.9151 | 328.63 | 14.5246 | 303.018 | 234.739 |  |  | 428.998 | 219.151 | 488.283 | 373.479
240.07 | 3.571 | 244.186 | 6.2205 | 363.555 | 4.3312 | 315.113 | 17.1302 | 302.497 | 307.584 |  |  | 427.771 | 280.174 | 487.724 | 473.392
222.723 | 4.2369 | 231.813 | 7.2634 | 348.602 | 4.8348 | 303.06 | 20.0022 | 302.324 | 378.647 |  |  | 427.526 | 363.354 | 487.166 | 592.522
208.498 | 5.007 | 221.391 | 8.4136 | 333.93 | 5.4349 | 289.146 | 25.3263 | 301.805 | 466.931 |  |  | 427.526 | 440.945
195.182 | 5.8994 | 212.285 | 9.707 | 321.157 | 6.0729 | 277.253 | 31.4641 | 301.632 | 558.586 |  |  | 426.304 | 538.794
184.737 | 6.8472 | 203.35 | 11.2553 | 304.579 | 7.0346 | 267.717 | 38.2386 | 301.114 | 598.318 |  |  | 427.526 | 596.607
174.501 | 8.0032 | 195.572 | 13.0246 | 293.222 | 7.8291 | 259.805 | 46.5649
168.331 | 8.8804 | 188.846 | 15.0721 | 282.289 | 8.792 | 251.371 | 58.724
162.216 | 9.8932 | 182.168 | 17.6696 | 272.307 | 9.9726 | 243.698 | 76.161
157.108 | 11.0104 | 175.903 | 20.8394 | 261.368 | 11.5057 | 236.733 | 99.968
151.249 | 12.8179 | 170.533 | 24.5778 | 250.618 | 13.3811 | 231.581 | 128.747
146.633 | 14.6852 | 166.656 | 28.4414 | 243.211 | 15.057 | 227.223 | 166.309
140.18 | 17.9905 | 162.379 | 34.3928 | 236.969 | 17.0107 | 223.84 | 214.831
136.31 | 20.632 | 159.641 | 40.1992 | 229.736 | 19.6454 | 220.287 | 283.965
131.885 | 24.5042 | 157.108 | 47.4581 | 223.616 | 22.6202 | 216.79 | 386.778
128.243 | 28.958 | 154.305 | 57.3314 | 217.877 | 26.2547 | 214.848 | 502.629
125.202 | 34.1187 | 152.008 | 69.2587 | 213.136 | 30.2909 | 214.419 | 599.954
122.6 | 40.1189 | 150.345 | 82.8349 | 208.707 | 35.0174
120.413 | 47.0329 | 148.551 | 104.256 | 204.37 | 40.8476
118.147 | 57.5612 | 146.633 | 130.823 | 200.323 | 47.696
116.504 | 68.8444 | 144.884 | 181.971 | 196.749 | 56.8746
114.77 | 82.0927 | 143.012 | 254.131 | 193.433 | 67.8873
113.174 | 99.868 | 141.873 | 339.289 | 190.172 | 81.1946
111.936 | 126.83 | 140.883 | 471.94 | 186.78 | 99.968
110.933 | 172.405 | 140.321 | 585.141 | 183.999 | 121.007
110.38 | 220.269 | 140.18 | 599.954 | 181.26 | 154.447
109.72 | 279.737 |  |  | 179.098 | 188.642
109.173 | 342.014 |  |  | 176.431 | 239.332
108.737 | 445.346 |  |  | 174.85 | 290.281
108.628 | 574.128 |  |  | 172.592 | 391.448
108.628 | 599.954 |  |  | 171.388 | 540.153
|  |  |  | 171.046 | 599.954